## Slide 1
EPS Meter Data Anomaly Observed During Black Start Testing for 2017
May 16, 2018

## Slide 2
Observation of an anomaly in EPS Meter Data at a generation facility during 2017 black start testing
Site configuration
  Generation site has configuration such that it can feed multiple transmission lines from the station
  Breakers allow for isolation of transmission lines
  Generation site uses voltage throw-over relays with a primary and secondary set of metering voltage transformers
  Primary and Back-up meters are connected to the same voltage transformer for normal operating conditions

## Slide 4
Scenario
  Line switching and isolation of circuits resulted in metering voltage transformers being sourced from a different system voltage than the system voltage where the generators were interconnected
  Current transformers, being in series with generation energy flows, use the same voltage reference as the generator interconnection

## Slide 6
Result
  EPS Meter voltage reference was sourced from one system voltage while the EPS Meter current was synchronized with a different system voltage
Anomaly
  With separate current and voltage sources, at slightly different frequencies, the energy being measured by the EPS Meter was constantly shifting between load and generation

## Slide 7
Discussion
  Different voltage throw-over wiring configurations
    Primary and Back-up meters on separate metering voltage transformers for normal operating conditions
    Primary and Back-up meters on same metering voltage transformer for normal operating conditions
TDSP | # of Sites | % of Sites | # Metering Ponits | % of Metering Points
Same transformer | 1 | 0.23% | 5 | 0.67%
Same transformer | 2 | 0.46% | 5 | 0.67%
Same transformer | 1 | 0.23% | 4 | 0.54%
Same transformer | 1 | 0.23% | 3 | 0.40%
Same transformer | 3 | 0.69% | 3 | 0.40%
Separate transformers | 28 | 6.48% | 84 | 11.32%
Same transformer | 1 | 0.23% | 1 | 0.13%
Same transformer | 1 | 0.23% | 2 | 0.27%
Same transformer | 5 | 1.16% | 14 | 1.89%
Same transformer | 1 | 0.23% | 3 | 0.40%
Same transformer | 1 | 0.23% | 1 | 0.13%
TOTAL | 45 | 10.42% | 125 | 16.85%

## Slide 8
Discussion
  Does the configuration where the primary and back-up meters are on separate metering voltage transformers for normal operating conditions minimize exposure to this anomaly?
  What if any action is needed to for similar site configurations where primary and secondary metering voltage transformers are utilized in metering schemes?