## Slide 1
ERCOT Frequency Control Report
April 2018
ERCOT
Operations Planning
PDCWG | May 9th, 2018

## Slide 2: Frequency Control
CPS1, BAAL, & RMS1

## Slide 3: Hourly CPS1 by Day
Apr-18 CPS1 (%): 175.93
Notes: Outliers
4/14/18 at 19:00 – 59.11% - Large expected generation deviation over the hour (down ~1900 MW) and ACEI and reg up exhausted. Wind and Solar ramping down. (~30 mins under 60Hz) and load on up ramp

## Slide 4: BAAL Exceedances & Violations
There were no BAAL exceedances

## Slide 5: 15-Minute Average CPS1%
Apr-18 CPS1 (%): 175.93

## Slide 6: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 176.90%

## Slide 7: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 14.2 mHz

## Slide 8: Daily RMS1 of ERCOT Frequency by Month

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 14.68 mHz
Min: 12.82 mHz
Max: 18.26 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: BAL-003 Selected Events
Notes: Frequency Bias updated from 764 to 759 in April

## Slide 19: Current BAL-003 FRM Performance
Notes: Put in some history of what these values were
Updated quarterly

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 25,900,024 Mwh

## Slide 22: Total Energy from Wind Generation
Notes: 6,721,813

## Slide 23: % Energy from Wind Generation
Notes: 25.95%

## Slide 24: ERCOT System Inertia

## Slide 25: Daily Minimum System Inertia
Notes: Minimum Inertia = 130,014 MW*s on 10/27/2017. This was also our record wind day.
Apr:
Mean: 165,290
Max: 195,435 on Apr 23rd
Min: 145,361 on Apr 3rd

## Slide 26: Questions?
Thank you!