## Slide 1
ERCOT Frequency Control Report
February 2018
ERCOT
Operations Planning
PDCWG | March 7th, 2018

## Slide 2: Frequency Control
CPS1, BAAL, & RMS1

## Slide 3: Hourly CPS1 by Day
Feb-18 CPS1 (%): 176.49
Notes: Outliers
2/1/18 at 04:00 - 42.9% - Large Down Wind Ramp Loss of 1500 MW over the hour and reg up exhausted. (~30 mins under 60Hz) and load on up ramp
2/10/18 at 10:00 – 84.7% - Large Down Wind Ramp Loss of 1700 MW over the hour and reg up exhausted. (~30 mins under 60Hz) and load on up ramp
2/16/18 at 12:00 – 96.5% - Large Down Wind Ramp Loss of 2400 MW over the hour and reg up exhausted. (~30 mins under 60Hz) and load on up ramp
2/16/18 at 13:00 – 87.1% - Large Down Wind Ramp Loss of 1096 MW over the hour and reg up exhausted. (~30 mins under 60Hz) and load on up ramp

## Slide 4: BAAL Exceedances & Violations
There were 2 BAAL exceedances
  February 5th 2018
    FME at 14:04:45
    Loss of 816 MW
    Less than 59.91 for 2 minutes

## Slide 5: 15-Minute Average CPS1%
Feb-18 CPS1 (%): 176.49

## Slide 6: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 175.86%

## Slide 7: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 14.50 mHz

## Slide 8: Daily RMS1 of ERCOT Frequency by Month

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 14.50 mHz
Min: 12.92 mHz
Max: 18.15 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary

## Slide 17: Hours on Time Error Control

## Slide 18: Number of Time Error Corrections

## Slide 19: BAL-003 Performance

## Slide 20: BAL-003 Selected Events

## Slide 21: Current BAL-003 FRM Performance
Notes: Put in some history of what these values were
Updated quarterly

## Slide 22: ERCOT Energy Statistics

## Slide 23: Total Energy
Notes: 31,278,046

## Slide 24: Total Energy from Wind Generation
Notes: 6,250,264

## Slide 25: % Energy from Wind Generation
Notes: 19.98%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 130,014 MW*s on 10/27/2017. This was also our record wind day.
Feb:
Mean: 186,900
Max: 242,865 on Feb 22nd
Min: 143,362 on Feb 1st

## Slide 28: Questions?
Thank you!