## Slide 1
ERCOT Frequency Control Report
January 2018
ERCOT
Operations Planning
PDCWG | February 14th, 2018

## Slide 2: Frequency Control
CPS1, BAAL, & RMS1

## Slide 3: Hourly CPS1 by Day
Jan-18 CPS1 (%): 178.79
Notes: No Outliers for December

## Slide 4: BAAL Exceedances & Violations
There were no BAAL exceedances

## Slide 5: 15-Minute Average CPS1%
Jan-18 CPS1 (%): 178.79
Notes: Hour 6 is lowest CPS by 15 minute at 151%

## Slide 6: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 175.51%

## Slide 7: Daily RMS1 of ERCOT Frequency by Year
Notes: Outlier was 10.7 mHz on Jan 2nd
Mean is 13.75 mHz

## Slide 8: Daily RMS1 of ERCOT Frequency by Month

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 13.75 mHz
Min: 10.71 mHz
Max: 16.59 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Hourly Time Error with STLF Error
Notes: Shows hourly data for the 16th and 17th of January
Ice day was the 16th
Large STLF Error ~300
Accumulating Negative Time Error on 16th
Accumulating Positive Time Error on 17th

## Slide 17: Hourly Time Error with Ace Intgeral
Notes: 16th and 17th data again
Now showing Ace Integral being largely negative and capped
Unable to adjust to STLF error so continue to gain negative errror

## Slide 18: Frequency Profile
Notes: We spent a lot of time on the lower end of 60 Hz on the 16th
Recovered time error on 17th by spending more time on the upper end of 60 Hz

## Slide 19: Time Error Corrections Log Summary

## Slide 20: Hours on Time Error Control

## Slide 21: Number of Time Error Corrections

## Slide 22: BAL-003 Performance

## Slide 23: BAL-003 Selected Events

## Slide 24: Current BAL-003 FRM Performance
FRM Performance Results for 2017 | 
2017 | Current data year (December thru November)
-381.0 | Operating Year 2018 BA Frequency Response Obligation (FRO) for next year's FRM
-381.0 | Operating Year 2017 BA Frequency Response Obligation (FRO)
-743.27 | 2017 FRM - Median Estimated Frequency Response MW/0.1Hz for BA Compliance to R1, minimum Frequency Response
-812.3 | 2017 FRM - Average Estimated Frequency Response MW/0.1 Hz using SEFRD for R1
0.0 | 2017 FRM - Regression Estimated Frequency Response MW/0.1Hz using SEFRD for R1
Notes: Put in some history of what these values were
Updated quarterly

## Slide 25: ERCOT Energy Statistics

## Slide 26: Total Energy
Notes: 31,278,046

## Slide 27: Total Energy from Wind Generation
Notes: 6,250,264

## Slide 28: % Energy from Wind Generation
Notes: 19.98%

## Slide 29: ERCOT System Inertia

## Slide 30: Daily Minimum System Inertia
Notes: Minimum Inertia = 130,014 MW*s on 10/27/2017. This was also our record wind day.
Jan:
Mean: 208,502
Max: 331,839 on Jan 2nd
Min: 138,977 on Jan 21st

## Slide 31: Questions?
Thank you!