## Slide 1
ERCOT Frequency Control Report
March 2018
ERCOT
Operations Planning
PDCWG | April 11th, 2018

## Slide 2: Frequency Control
CPS1, BAAL, & RMS1

## Slide 3: Hourly CPS1 by Day
Mar-18 CPS1 (%): 177.94
Notes: Outliers
3/11/18 at 19:00 – 100.5% - Large Down Wind Ramp Loss of 2750 MW over the hour and reg up exhausted. (~30 mins under 60Hz) and load on up ramp

## Slide 4: BAAL Exceedances & Violations
There were no BAAL exceedances

## Slide 5: 15-Minute Average CPS1%
Mar-18 CPS1 (%): 177.94

## Slide 6: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 176.58%

## Slide 7: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 14.1 mHz

## Slide 8: Daily RMS1 of ERCOT Frequency by Month

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 14.06 mHz
Min: 11.69 mHz
Max: 16.66 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: BAL-003 Selected Events
Notes: Frequency Bias updated from 764 to 759 in April

## Slide 19: Current BAL-003 FRM Performance
Notes: Put in some history of what these values were
Updated quarterly

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 26,308,449 Mwh

## Slide 22: Total Energy from Wind Generation
Notes: 6,638,110
Updated February 2015 data

## Slide 23: % Energy from Wind Generation
Notes: 25.23%

## Slide 24: ERCOT System Inertia

## Slide 25: Daily Minimum System Inertia
Notes: Minimum Inertia = 130,014 MW*s on 10/27/2017. This was also our record wind day.
Mar:
Mean: 173,418
Max: 211,981 on Mar 6th
Min: 145,695 on Mar 9th

## Slide 26: Questions?
Thank you!