## Slide 1
Grapevine Switching Station Project - ERCOT Independent Review
ERCOT Transmission Planning
Regional Planning Group
May 22nd, 2018

## Slide 2: Overview
ONCOR submitted the Grapevine Switching Station Project
Tier 2 project estimated cost of $25 million
Proposed for the 2019 timeframe
Reliability Issues
    Voltage Collapse
    Consequential Load Loss

## Slide 3: Grapevine Switching Station
Source: Oncor report filed with RPG on Feb 9th 2018

## Slide 4: Grapevine Project Key Changes
12 breakers at Grapevine Sw Sta in breaker and a half layout
Roanoke – Grapevine Sw Sta 138 kV line
Two Euless – Grapevine Sw Sta 138 kV lines
McKamy to Grapevine Sw Sta and two Coppell – Grapevine Sw Sta 138 kV lines – Triple circuit structure
Hackberry to Grapevine Sw Sta 138 kV line

## Slide 5: Steady State Study Assumptions
2017 RTP Reliability Case: 17RTP_2019_SUM_NNC
Area of Study: North and North-Central Weather Zones
Generator additions which meet Planning Guide Section 6.9
Transmission Projects from February 2018 TPIT Spreadsheet
NERC TPL-001-4 and ERCOT Planning Criteria* were assessed

## Slide 6: Preliminary Study Results
Pre project results show a voltage collapse in the Grapevine area under N-1-1
Bus | Name | Voltage (in Per Unit) |  | % Drop
 |  | N-1 | N-1-1 | 
658 | MCKAMY | 1.00 | 0.635 | 36.50
2024 | MCKAMYRD_8 | 1.00 | 0.635 | 36.50
2031 | FLWRMNDS1_8 | 1.00 | 0.638 | 36.20
660 | LEWISVILLE | 1.03 | 0.644 | 38.60
656 | MOUND | 1.01 | 0.645 | 36.50
2025 | MCKAMY_T8 | 1.01 | 0.645 | 36.50
2015 | COPPELL_8 | 1.01 | 0.646 | 36.40
648 | COPPELL | 1.01 | 0.646 | 36.40
555 | GRAPEVINE | 1.00 | 0.732 | 26.80
556 | IBM | 1.00 | 0.754 | 24.60

## Slide 7: Preliminary Study Results – Grapevine Project Implemented
Contingency (NERC/ERCOT) reliability requirements | Violation
P0/P1/P7 | None
P3 (G-1+N-1) | None
P6 (X-1+N-1) | None
Voltage violations of concern are resolved with this new project under N-1-1 conditions

## Slide 8: Next Steps
ERCOT is looking at possible alternatives if any
Final Results and Report in June RPG

## Slide 9
?
Any Stakeholder Comments: rpg@ercot.com