## Slide 1
Far West Texas Project 2 and Dynamic Reactive Devices -
ERCOT Independent Review
TAC
May 24, 2018

## Slide 2: Overview
Oncor submitted Far West Texas Project 2 (FWTP2) and Dynamic Reactive Devices (DRD) for Regional Planning Group review. Both are Tier 1 project that were estimated to cost $86 million for DRD project and $194 million for FWTP2 project.
  Proposed for both 2019 to 2023 timeframe
  Addresses oil and gas related load growth
  Reliability Issues
    Voltage Collapse
    Loss of Load
  Provide Operational Flexibility
  Provides future upgrade path for Far West Region

## Slide 3: Project Needs
Scenario | Load (MW) | Transmission Upgrades | Culberson Load Serving Capability | 
 |  |  | NERC P1, P7 | NERC P6
1. | 880 (2019 Summer Peak) | None | Collapse in Base Case | 
2. | 880 (2019 Summer Peak) | FWTP* | Voltage Violation Voltage Collapse | Voltage Violation Voltage Collapse
Steady State Voltage Stability Assessment for the Base Case Condition
*The Far West Texas Project (FWTP) endorsed by ERCOT Board of Directors in June, 2017.

## Slide 4: Options Considerations
ERCOT short-listed only options that included a second 345 kV circuit to the Odessa EHV-Riverton (between Moss and Riverton), Sand Lake-Solstice, and Solstice-Bakersfield 345 kV lines for the following reasons:
  Significant load growth in the Culberson loop
  Operational flexibility
  Cost saving, ~50% less than the cost of coming back to install the second circuit at a later time
The new 138 kV lines proposed in the FWTP2 are necessary to strengthen the Culberson Loop and provide operational flexibility under normal and outage conditions.
Reactive support needs for both near term and long term load growth.
Three options (included in Appendix) were selected for detailed analysis.

## Slide 5: Comparison of Project Options
Note:
(1). Dynamic stability was conducted at the Culberson load level identified in the PV voltage collapse results.
(2). Assuming reactive devices will be in service before new transmission lines.
 | Culberson Loop Load Served (MW) |  | 
Description | Option 1 | Option 2 | Option 3
PV Voltage Collapse Results (NERC P1, P6, P7, ERCOT Events) | 1608 | 1568 | 1688
Dynamic Stability Result (without PBSES Units) (NERC P1, P6, P7, ERCOT Events)(1) | Acceptable | Acceptable | Acceptable
Estimated Capital Cost ($M) | 300 | 292.5 | 327.5
PV Voltage Collapse Results (reactive devices only(2) (NERC P1, P6, P7, ERCOT Events) | 801 | 821 | 1001

## Slide 6: Subsynchronous Resonance (SSR) Vulnerability Assessment – Protocol Section 3.22.1.3(2)
All three short-listed options strengthen the transmission network and increase the required transmission circuit outages to have a Generation Resource become radial to series capacitors.
The SSR assessment results showed no SSR vulnerability for any existing Generation Resources or Generation Resources satisfying Planning Guide Section 6.9 conditions for inclusion in the planning models at the time of this study.

## Slide 7: Sensitivity Analysis – PG Section 3.1.3 (4)
ERCOT concludes that the generation sensitivity analysis as described in PG Section 3.1.3 (4)(a) did not have an impact on the project need on the three project options
ERCOT concludes that the load scaling as described in PG Section 3.1.3 (4)(b) did not have an impact on the project need and any of the three project options

## Slide 8: ERCOT Recommendation:
Based on the review, ERCOT will recommend the Board endorse Option 3 to address the reliability need in the study region:
Estimated Capital Cost: $327.5 million
ERCOT will recommend that the Board deems the Riverton – Sand Lake 345 kV line, the Sand Lake – Solstice 345 kV line, and the Bakersfield – Solstice 345 kV line project critical to reliability

## Slide 9: ERCOT Recommendation: Option 3
Construct a new approximately 40-mile 345 kV line on double-circuit structures with two circuits in place from Sand Lake 345 kV Switch Station to Solstice 345 kV Switch Station
Add two new 600 MVA, 345/138 kV autotransformers at Sand Lake 345 kV Switch Station
Install a new 345 kV circuit on the planned Riverton – Sand Lake double circuit structures
Install the second 345 kV circuit on the Odessa EHV – Riverton 345 kV line double circuit structures between Moss and Riverton (creating a Moss – Riverton 345 kV circuit)
Construct a new Quarry Field 138 kV Switch Station in the Wink – Riverton double-circuit 138 kV line
Construct a new approximately 20-mile Kyle Ranch – Riverton 138 kV line on double-circuit structures with one circuit in place from Kyle Ranch 138 kV Substation to Riverton 138 kV Switch Station
Construct a new approximately 20-mile Owl Hills – Tunstill – Riverton 138 kV line on double circuit structures with one circuit in place from Owl Hills 138 kV Switch Substation to Riverton 138 kV Switch Station
Install the second 345 kV circuit on the planned Solstice 345 kV Switch Station – Bakersfield 345 kV Switch Station double circuit structures
Install one 250 MVAR STATCOM at Horseshoe Springs 138 kV Switch Station
Install one 250 MVAR STATCOM at Quarry Field 138 kV Switch Station
Install 150 MVAR static capacitors at Horseshoe Springs 138 kV Switch Station
Install 150 MVAR static capacitors at Quarry Field 138 kV Switch Station

## Slide 10: Option 3
?

## Slide 11
Appendix

## Slide 15: Culberson Loop Area Load Growth
    Existing and confirmed load requests of 880 MW by 2019
    Existing, confirmed, and conceptual load of 1347 MW by 2023