## Slide 1
Reliability Unit Commitment
Agee Springer
Supervisor, Engineer Development Program
2018 Operator Training Seminar

## Slide 2: Objectives
Review the purpose and timeline of the Reliability Commitment process
Identify the steps the RUC engine takes to make commitment recommendations
Identify the impacts of decisions made by ERCOT and QSEs in the RUC process

## Slide 3: Today’s Agenda
RUC Fundamentals
The RUC Engine
Control Room Analysis and Actions
Post-RUC Actions and Impact

## Slide 4: Today’s Agenda
RUC Fundamentals
The RUC Engine
Control Room Analysis and Actions
Post-RUC Actions and Impact

## Slide 5: What is RUC?
RUC is an acronym for Reliability Unit Commitment
RUC ensures…
  Enough capacity is committed to serve forecasted load
  Committed capacity is in the right locations

## Slide 6: RUC Considerations – Capacity
When evaluating capacity, RUC differentiates between dispatchable generation and Ancillary Services
Capacity that is reserved for AS is unavailable to RUC
If AS will be needed to meet projected load, RUC will commit additional generation to ensure there is enough dispatchable capacity available
Dispatchable Capacity
AS Capacity
RUC Commit
AS Capacity
Load Forecast
Not available to RUC

## Slide 7: RUC Considerations – Locational
When deciding which resources to commit, RUC evaluates several factors:
  Resource constraints
  Transmission constraints
  Resource startup and minimum energy costs
This ensures generation is committed in the right locations to maintain grid reliability while minimizing costs

## Slide 8: Where RUC Fits

## Slide 9: When are RUC Studies Executed
There are three RUC sequences:
  Weekly (WRUC)
  Day-Ahead (DRUC)
  Hourly (HRUC)
These are executed at different times during the Operating Day and study different timeframes.
Day 1
Day 2
Notes: We don’t commit units in WRUC – will not be talking about it in this presentation

## Slide 10: When are RUC Studies Executed
Day-Ahead RUC (DRUC)
  Executed after the completion of the Day-Ahead Market (DAM) plus a period for COP updates, typically at 14:30
  Evaluates each hour of the next Operating Day
DRUC Study Period
Day 1
Day 2
1430
DRUC runs

## Slide 11: When are RUC Studies Executed
Hourly RUC (HRUC)
  Executed hourly
  Evaluates all remaining hours in the current Operating Day plus all hours of the next OD after the completion of DRUC
DRUC Study Period
Day 1
Day 2
1430
DRUC runs
HRUC runs each hour
0000
0100
0200
1600
1700
1800

## Slide 12: RUC Results
All commitments/decommitments made in each RUC run (DRUC or HRUC) are presented as recommendations to the operator
The operator may accept all, some, or none of these recommendations and may also manually commit additional units before approving the RUC results
Once approved, the RUC results are sent to the affected QSEs via XML message
RUC commitments may also be communicated via Verbal Dispatch Instruction (VDI)

## Slide 13: Today’s Agenda
RUC Fundamentals
The RUC Engine
Control Room Analysis and Actions
Post-RUC Actions and Impact

## Slide 14: RUC Engine – Overview
Reliability Unit
Commitment Engine
Transmission
Security Analysis
(TSA)
Reliability Unit Commitment
(RUC)
Current Operating Plans (COPs)
Network
Operations
Model
Contingencies
Load Forecast
Offers
Resource Commitments
Resource De-commitments
Constraint Information
Additional Resource Information
RUC Input
RUC Engine Process
RUC Output

## Slide 15: RUC Engine – Inputs
Tells RUC which units are committed (ON), offline but available (OFF), or unavailable (OUT).
Includes equipment ratings, transmission outages, etc.
Includes all current valid contingencies.
Load forecast by hour and includes current Load Distribution Factors (LDFs).
High and Low Sustained Limits (HSL), Ancillary Service (AS) responsibilities, start time, start type (hot, warm, cold), min online time, etc.
Current Operating Plans (COPs)
Network
Operations
Model
Contingencies
Load Forecast
Additional Resource Information

## Slide 16: RUC Engine
The RUC Engine is made up of two blocks
The first is a Transmission Security Analysis (TSA)
The second is the Reliability Unit Commitment (RUC)
These two steps are looped until a satisfactory result is reached
RUC Engine
Transmission
Security
Analysis
(TSA)
Reliability Unit Commitment
(RUC)

## Slide 17: RUC Engine
Determine initial unit commitment
  Occurs in the RUC block
  Resources that have previously committed (through DAM, earlier RUCs, and self-commitments) are optimally dispatched to meet load forecast
  Additional resources may be committed if existing generation is not sufficient.
  Transmission constraints are not considered
RUC Engine
Transmission
Security
Analysis
(TSA)
Reliability Unit Commitment
(RUC)

## Slide 18: RUC Engine – Three Part Offers
When evaluating resources for commitment, the RUC block looks at
  Startup Offer (if applicable)
  Minimum Energy Offer
The Energy Offer Curve is not used when making a commitment decision
RUC Engine
Transmission
Security
Analysis
(TSA)
Reliability Unit Commitment
(RUC)
Offers
Energy Offer Curve
Startup Offer
Cost up to LSL
($/Start)
Minimum Energy Offer
Cost per hour at LSL
($/MWh)
Reliability Unit Commitment
(RUC)

## Slide 19: RUC Engine
Security analysis of initial dispatch solution
  Dispatch solution from RUC block is provided to the TSA block
  A security analysis is performed that considers both the base case and contingency conditions
  A list of binding and violated constraints is generated
RUC Engine
Transmission
Security
Analysis
(TSA)
Reliability Unit Commitment
(RUC)

## Slide 20: RUC Engine
Determine revised unit commitments
  List of binding/violated constraints from the TSA block is provided to the RUC block
  These constraints are then enforced in the RUC block
  Online units are optimally re-dispatched and additional generation is committed as needed to resolve the constraints
RUC Engine
Transmission
Security
Analysis
(TSA)
Reliability Unit Commitment
(RUC)

## Slide 21: RUC Engine
Security analysis of revised dispatch solution
  Dispatch solution from the latest RUC block run is provided to the TSA block
  A security analysis is performed that considers both the base case and contingency conditions
  A list of binding and violated constraints is generated
RUC Engine
Transmission
Security
Analysis
(TSA)
Reliability Unit Commitment
(RUC)

## Slide 22: RUC Engine
Steps 3 and 4 are looped until
The TSA shows all constraints have been resolved
OR
There are no units that can be committed to resolve any remaining constraints
RUC Engine
Transmission
Security
Analysis
(TSA)
Reliability Unit Commitment
(RUC)

## Slide 23: RUC Engine – Outputs
Presented as recommendations to the ERCOT Operator
Operator must review and may make changes manually
Detailed information on contingency, overloaded element, ratings and flows, unit shift factors, etc.
Presented as informational to the Operator to assist in analysis
Resource Commitments
Resource De-commitments
Constraint Information

## Slide 24: Today’s Agenda
RUC Fundamentals
The RUC Engine
Control Room Analysis and Actions
Post-RUC Actions and Impact

## Slide 25: Control Room Activities
Once the RUC sequence has completed, the Operator reviews multiple screens
These screens contain the results of the study as well as details on how RUC arrived at its recommendations
The Operator uses this information to make final commitment decisions

## Slide 26: MMS Displays
The Commitment/Decommitment Analysis display gives the operator an overview of RUC recommendations
  Hours where commitment is recommended are highlighted
  Reason for commitment indicated by color
  Other unit information (startup type, min online time, HSL/LSL, etc.) is also shown

## Slide 27: MMS Displays
The Operator may click on a highlighted hour, bringing up the Resource to Constraint Details display

## Slide 28: MMS Displays
The Operator may click on a highlighted hour, bringing up the Resource to Constraint Details display
  Shows all constraints that were binding for that hour
  Shows shift factor for the selected resource on each constraint
  Shows the flow and shadow price at the end of the RUC solution for each constraint

## Slide 29: MMS Displays
If the Operator needs additional information, a Suggestion Plan can be generated
  Gives detailed information for a single constraint in a single hour (e.g. constraint A in HE 17)
  Allows the Operator to see if a suggested commitment is reasonable or to identify other impactful units if additional commitments are needed

## Slide 30: MMS Displays
For each unit, the Suggestion Plan shows
  Final MW dispatch for each unit
  The MW impact the unit had on a constraint as a result
  Whether the unit was selected by RUC for commitment

## Slide 31: MMS Displays
The Commitment/Decommitment Summary page is then use to finalize the commitment decisions
  Suggested units are automatically entered
  The Operator may manually add or remove units
  A reason must be entered for all commitments and manual actions

## Slide 32: Making Commitment Decisions
While the RUC tool makes suggestions, it is the Operator that is ultimately responsible for making commitment decisions
Several factors go into deciding these outcomes

## Slide 33: Making Commitment Decisions
Possible reasons for deciding not to commit a unit recommended by RUC:
Evaluate Later: RUC suggestion is valid but the unit’s start time allows for the decision to be deferred until a later HRUC run.
Short Start: RUC suggestion is valid but the unit has a start time of <1 hour.
A review of load forecast, weather forecast, COP data, and additional real-time studies has shown the unit is not needed.

## Slide 34: Making Commitment Decisions
Possible reasons for deciding to accept a RUC recommendation:
Capacity: Unit is needed to ensure adequate system-wide capacity
Contingency: Unit is needed to manage congestion. The specific contingency will be entered as the Reason for commitment.
Valley Import: Specific reason given for the Valley Import GTC

## Slide 35: Making Commitment Decisions
Possible reasons for manually committing a unit that was not recommended by RUC:
Voltage Support: The RUC tool cannot see voltage contingencies. Must be identified in additional study and committed manually.
Forced outage occurred after RUC run was initiated.
A review of load forecast, weather forecast, COP data, and additional real-time studies has shown the unit is needed

## Slide 36: Today’s Agenda
RUC Fundamentals
The RUC Engine
Control Room Analysis and Actions
Post-RUC Actions and Impact

## Slide 37: Responsibilities after a RUC
Once a decision to commit a unit has been reached, both ERCOT and the QSE have defined responsibilities:
The communication may be electronic or verbal
ERCOT: | QSE:
Communicates the start interval and duration for which the Resource is required to be at least LSL | Acknowledges receipt of RUC and updates COP to confirm RUC status Updates Energy Offer Curve for RUC status

## Slide 38: Responsibilities after a RUC
When a QSE receives a RUC instruction, it has two options for how to proceed:
  The QSE may choose to go ONRUC
  The QSE may choose to buy-back the RUCed hours and go ONOPTOUT
Each option has different operational and financial implications
The resource must still be online for all RUCed hours regardless of which option is chosen

## Slide 39: Going ONRUC – Operational Impacts
Energy Offer Curve
If the QSE elects to go ONRUC
All energy above LSL is subject to an offer floor of $1500
The QSE may update the Energy Offer Curve by the end of the Adjustment Period
  ERCOT will update it automatically if the QSE does not
The Reliability Deployment Price Adder will be triggered for all other online units
$1500
LSL
HSL

## Slide 40: Going ONRUC – Financial Impact
If the QSE elects to go ONRUC
ERCOT guarantees the QSE will recover its Start-up and Minimum Energy Costs
  QSE must actually incur the costs
  Start-up cost only paid if the unit start was due to the RUC instruction
Minimum Energy Costs
Startup Costs
Costs Incurred

## Slide 41: Going ONRUC – Financial Impact
This means the QSE will receive a make-whole payment if revenue is less than costs
Make-Whole Payment
Real-Time Revenue
less
Incremental Costs
Minimum Energy Costs
Startup Costs
$
Revenues Received
Costs Incurred
RUC Guaranteed Amount

## Slide 42: Going ONRUC – Financial Impact
However, the QSE may receive a claw-back charge for revenues beyond the RUC guaranteed amount
Real-Time Revenue
less
Incremental Costs
Minimum Energy Costs
Startup Costs
$
Revenues Received
Costs Incurred
Claw-Back Charge
RUC Guaranteed Amount

## Slide 43: Going ONOPTOUT – Operational Impacts
If the QSE elects to go ONOPTOUT
The resource must still start/run for the all RUCed hours
No $1500 floor for energy
Unit is dispatched normally according to its Energy Offer Curve
The Reliability Deployment Price Adder is not triggered
Energy Offer Curve
$ / MWh

## Slide 44: Going ONOPTOUT – Financial Impact
No RUC financial settlements apply for resources that elect to go ONOPTOUT
This means there is no claw-back charge for any profits made during the RUC hours
However, there is also no make-whole payment if revenue is less than costs

## Slide 45: How to Opt-out of a RUC Instruction?
When a QSE receives a RUC instruction, the COP should be updated to reflect the intended opt-out decision (ONRUC or ONOPTOUT) for future hours
However, with the implementation of NPRR744 in 2017, the COP update does not constitute a decision to opt-out
The determination of whether the resource has opted-out is now based on the telemetered resource status

## Slide 46: How to Opt-out of a RUC Instruction?
In order to opt-out of a RUC instruction, the QSE must telemeter a status of ONOPTOUT in the first SCED interval during the RUC block where the unit is online and available for SCED dispatch
This means…
  If the unit is offline prior to the RUC, the QSE must telemeter ONOPTOUT for the first SCED interval after the unit exits STARTUP
  If the RUC is extending a unit already online, the QSE must telemeter ONOPTOUT for the first SCED interval of the RUC block

## Slide 47: How to Opt-out of a RUC Instruction?
Some things to note:
Any online telemetered status (ON, ONREG, etc.) that is not ONOPTOUT is treated as ONRUC by SCED
The opt-out decision is recorded automatically in the first SCED interval and cannot be changed for the remainder of the RUC block
The first available SCED interval must occur in the first hour of the RUC block in order to opt-out
  If the unit fails to start in the first hour, it cannot opt-out and will be considered ONRUC when it comes online

## Slide 48: How to Opt-out of a RUC Instruction?
Some things to note:
Any changes to the telemetered resource status after the opt-out decision has been made will be automatically overridden by SCED back to either ONRUC or ONOPTOUT depending on the decision
The ERCOT Operator cannot override an opt-out decision once it has been made

## Slide 49: Opting-out: Examples
Consider the following scenario:
Unit A has been committed for HE 15 through HE 18. The unit is initially offline.
SCED Timestamp | Scenario 1
13:50 | STARTUP
13:55 | STARTUP
14:00 (start of RUC) | ONOPTOUT
14:05 | ONOPTOUT
14:10 | ONOPTOUT
14:15 | ONOPTOUT
14:20 | ONOPTOUT
SCED Timestamp | Scenario 1
13:50 | STARTUP
13:55 | STARTUP
14:00 (start of RUC) | ONOPTOUT
14:05 | ONOPTOUT
14:10 | ONOPTOUT
14:15 | ONOPTOUT
14:20 | ONOPTOUT
RESULT | Opt-out
SCED Timestamp | Scenario 1 | Scenario 2
13:50 | STARTUP | OFF
13:55 | STARTUP | OFF
14:00 (start of RUC) | ONOPTOUT | STARTUP
14:05 | ONOPTOUT | STARTUP
14:10 | ONOPTOUT | ONOPTOUT
14:15 | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | 
SCED Timestamp | Scenario 1 | Scenario 2
13:50 | STARTUP | OFF
13:55 | STARTUP | OFF
14:00 (start of RUC) | ONOPTOUT | STARTUP
14:05 | ONOPTOUT | STARTUP
14:10 | ONOPTOUT | ONOPTOUT
14:15 | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | Opt-out
SCED Timestamp | Scenario 1 | Scenario 2 | Scenario 3
13:50 | STARTUP | OFF | OFF
13:55 | STARTUP | OFF | STARTUP
14:00 (start of RUC) | ONOPTOUT | STARTUP | STARTUP
14:05 | ONOPTOUT | STARTUP | ONRUC
14:10 | ONOPTOUT | ONOPTOUT | ONRUC
14:15 | ONOPTOUT | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | Opt-out | 
SCED Timestamp | Scenario 1 | Scenario 2 | Scenario 3
13:50 | STARTUP | OFF | OFF
13:55 | STARTUP | OFF | STARTUP
14:00 (start of RUC) | ONOPTOUT | STARTUP | STARTUP
14:05 | ONOPTOUT | STARTUP | ONRUC
14:10 | ONOPTOUT | ONOPTOUT | ONRUC
14:15 | ONOPTOUT | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | Opt-out | RUC
SCED Timestamp | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4
13:50 | STARTUP | OFF | OFF | STARTUP
13:55 | STARTUP | OFF | STARTUP | STARTUP
14:00 (start of RUC) | ONOPTOUT | STARTUP | STARTUP | ON
14:05 | ONOPTOUT | STARTUP | ONRUC | ONOPTOUT
14:10 | ONOPTOUT | ONOPTOUT | ONRUC | ONOPTOUT
14:15 | ONOPTOUT | ONOPTOUT | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | Opt-out | RUC | 
SCED Timestamp | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4
13:50 | STARTUP | OFF | OFF | STARTUP
13:55 | STARTUP | OFF | STARTUP | STARTUP
14:00 (start of RUC) | ONOPTOUT | STARTUP | STARTUP | ON
14:05 | ONOPTOUT | STARTUP | ONRUC | ONOPTOUT
14:10 | ONOPTOUT | ONOPTOUT | ONRUC | ONOPTOUT
14:15 | ONOPTOUT | ONOPTOUT | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | Opt-out | RUC | RUC
 Interval SCED uses to determine opt-out decision

## Slide 50: Opting-out: Examples
Consider the following scenario:
Unit B has been committed for HE 15 through HE 18.
The unit was self-scheduled through HE 14 and RUC is extending the commitment.
SCED Timestamp | Scenario 1
13:50 | ON
13:55 | ON
14:00 (start of RUC) | ONOPTOUT
14:05 | ONOPTOUT
14:10 | ONOPTOUT
14:15 | ONOPTOUT
14:20 | ONOPTOUT
SCED Timestamp | Scenario 1
13:50 | ON
13:55 | ON
14:00 (start of RUC) | ONOPTOUT
14:05 | ONOPTOUT
14:10 | ONOPTOUT
14:15 | ONOPTOUT
14:20 | ONOPTOUT
RESULT | Opt-out
SCED Timestamp | Scenario 1 | Scenario 2
13:50 | ON | ON
13:55 | ON | ON
14:00 (start of RUC) | ONOPTOUT | ON
14:05 | ONOPTOUT | ONOPTOUT
14:10 | ONOPTOUT | ONOPTOUT
14:15 | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | 
SCED Timestamp | Scenario 1 | Scenario 2
13:50 | ON | ON
13:55 | ON | ON
14:00 (start of RUC) | ONOPTOUT | ON
14:05 | ONOPTOUT | ONOPTOUT
14:10 | ONOPTOUT | ONOPTOUT
14:15 | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | RUC
SCED Timestamp | Scenario 1 | Scenario 2 | Scenario 3
13:50 | ON | ON | ON
13:55 | ON | ON | ON
14:00 (start of RUC) | ONOPTOUT | ON | ONRUC
14:05 | ONOPTOUT | ONOPTOUT | ONRUC
14:10 | ONOPTOUT | ONOPTOUT | ONRUC
14:15 | ONOPTOUT | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | RUC | 
SCED Timestamp | Scenario 1 | Scenario 2 | Scenario 3
13:50 | ON | ON | ON
13:55 | ON | ON | ON
14:00 (start of RUC) | ONOPTOUT | ON | ONRUC
14:05 | ONOPTOUT | ONOPTOUT | ONRUC
14:10 | ONOPTOUT | ONOPTOUT | ONRUC
14:15 | ONOPTOUT | ONOPTOUT | ONOPTOUT
14:20 | ONOPTOUT | ONOPTOUT | ONOPTOUT
RESULT | Opt-out | RUC | RUC
 Interval SCED uses to determine opt-out decision

## Slide 51: Objectives – Review
Review the purpose and timeline of the Reliability Commitment process
Identify the steps the RUC engine takes to make commitment recommendations
Identify the impacts of decisions made by ERCOT and QSEs in the RUC process

## Slide 52: Questions?