| PGRR Number | 060 | PGRR Title | Clarification of Reliability Performance Criteria |
| --- | --- | --- | --- |
| Date of Decision |  | June 12, 2018 |  |
| Action |  | Approved |  |
| Timeline |  | Normal |  |
| Effective Date |  | July 1, 2018 |  |
| Priority and Rank Assigned |  | Not Applicable |  |
| Planning Guide Sections Requiring Revision |  | 4.1.1.2, Reliability Performance Criteria |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Planning Guide Revision Request (PGRR) updates the reliability performance criteria by defining unavailability of a Direct Current Tie (DC Tie) as a new contingency. The PGRR also includes clarification of the voltage level of transformers referred to in the reliability performance criteria. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | DC Ties are currently modeled based on historic import/export patterns. However, flows over the DC Ties are driven by market forces beyond ERCOT’s control and it is possible that assumed imports may not materialize in future operation. Additionally, it is possible that a DC Tie experiences a momentary or extended Forced Outage. This PGRR allows planners to evaluate and plan for unavailability or Outage of DC Tie Resources or DC Tie Load. |  |
| ROS Decision |  | On 3/1/18, ROS voted unanimously to recommend approval of PGRR060 as revised by ROS. All Market Segments were present for the vote. On 4/5/18, ROS voted unanimously to endorse and forward to TAC the 3/1/18 ROS Report and Impact Analysis for PGRR060. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 3/1/18, participants discussed revisions to PGRR060 proposed by the Planning Working Group (PLWG) at its February 26, 2018 meeting. On 4/5/18, there was no discussion. |  |
| TAC Decision |  | On 5/24/18, TAC voted unanimously to recommend approval of PGRR060 as recommended by ROS in the 4/5/18 ROS Report. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 5/24/18, there was no discussion. |  |
| ERCOT Opinion |  | ERCOT supports approval of PGRR060. |  |
| Board Decision |  | On 6/12/18, the ERCOT Board approved PGRR060 as recommended by TAC in the 5/24/18 TAC Report. |  |

| Sponsor |  |
| --- | --- |
| Name | Sandeep Borkar |
| E-mail Address | Sandeep.Borkar@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6642 |
| Cell Number | 501-246-0147 |
| Market Segment | N/A |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed Guide Language Revision

4.1.1.2	Reliability Performance Criteria

(1)	The following reliability performance criteria (summarized in Table 1, ERCOT-specific Reliability Performance Criteria, below) shall be applicable to planning analyses in the ERCOT Region:

(a)	With all Facilities in their normal state, following a common tower outage with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(b)	With all Facilities in their normal state, following an outage of a DC Tie Resource or DC Tie Load with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(c)	With any single generating unit unavailable, followed by Manual System Adjustments, followed by a common tower outage or outage of a DC Tie Resource or DC Tie Load with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(d)	With any single transformer, with the high voltage winding operated at 300 kV or above and low voltage winding operated at 100 kV or above unavailable, followed by Manual System Adjustments, followed by a common tower outage, or the contingency loss of a single generating unit, transmission circuit, transformer, shunt device, FACTS device, or DC Tie Resource or DC Tie Load with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.  An operational solution may be planned on a permanent basis to resolve a performance deficiency under this condition.

(e)	With any single DC Tie Resource or DC Tie Load unavailable, followed by Manual System Adjustments, followed by a common tower outage, or the contingency loss of a single generating unit, transmission circuit, transformer, shunt device, FACTS device, or DC Tie Resource or DC Tie Load, with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.  An operational solution may be planned on a permanent basis to resolve a performance deficiency under this condition.

| Initial Condition |  | Event | Facilities within Applicable Ratings and System Stable with No Cascading or Uncontrolled Outages | Non-consequential Load Loss Allowed |
| --- | --- | --- | --- | --- |
| 1 | Normal System | Common tower outage, DC Tie Resource outage, or DC Tie Load outage | Yes | No |
| 2 | Unavailability of a generating unit, followed by Manual System Adjustments | Common tower outage, DC Tie Resource outage, or DC Tie Load outage | Yes | No |
| 3 | Unavailability of a transformer with the high voltage winding operated at 300 kV or above and low voltage winding operated at 100 kV or above, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; 5. FACTS device; or 6. DC Tie Resource or DC Tie Load | Yes | No |
| 4 | Unavailability of a DC Tie Resource or DC Tie Load, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; 5. FACTS device; or 6. DC Tie Resource or DC Tie Load | Yes | No |

Table 1: ERCOT-specific Reliability Performance Criteria

(2)	ERCOT and the TSPs shall endeavor to resolve any performance deficiencies as appropriate.  If a Transmission Facility improvement is required to meet the criteria in this Section 4.1.1.2, but the improvement cannot be implemented in time to resolve the performance deficiency, an interim solution may be used to resolve the deficiency until the improvement has been implemented.