| PGRR Number | 062 | PGRR Title | Updates to Generation Interconnection or Change Request (GINR) Process |
| --- | --- | --- | --- |

| Date | June 6, 2018 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Jason Kemper |
| E-mail Address | Jason.Kemper@edf-re.com |
| Company | EDF Renewable Energy Inc. |
| Phone Number | 303-568-1277 |
| Cell Number | 928-863-1836 |
| Market Segment | Independent Generator |

Comments

EDF Renewables (EDF) appreciates the opportunity to comment on the interconnection issues under consideration by ERCOT in Planning Guide Revision Request (PGRR) 062, and offers the following:

The business case description for PGRR054, Stability Limits in the Full Interconnect Study, stated that there were concerns that the existing time table allows Full Interconnection Study (FIS) results to be released to an Interconnecting Entity (IE) prior to the FIS being available to all Market Participants.  While EDF understands this concern, the language approved in PGRR054 has also resulted in the omission of critical information that has historically been studied by the Transmission Service Provider (TSP) and shared with the IE during the FIS process.  An IE depends on the timely release and review of each preliminary FIS study element that occurs during the FIS process to direct the course of the project.  Depending on the preliminary results of each individual FIS study element before the complete set of FIS are deemed final, an IE may want to modify or even forgo a proposed project.  Waiting until the FIS is complete to share any information with the IE has resulted in a more inefficient development process.

EDF proposes that ERCOT send a copy of each preliminary report to the IE requesting the GINR within ten Business Days of the TSP’s delivery of each study element’s preliminary report to ERCOT and the other TSPs, and at the same time post a redacted copy of each study element’s preliminary report to the Market Information System (MIS) Secure Area.  This will allow all Market Participants to receive the same information at the same time, and allow the IE to have the preliminary information that is important to the development of the project.

Revised Cover Page Language

| Planning Guide Sections Requiring Revision | 5.2.1, Generation Interconnection or Change Request Application 5.2.2, Generation Interconnection or Change Request Submission Requirements 5.3, Full Interconnection Study Request 5.3.1, Full Interconnection Study Submission Requirements 5.3.2, Modifications to Request Declarations of Resource Data Accuracy 5.4.1, Security Screening Study 5.4.2.1, Full Interconnection Study Process Overview 5.4.7, Economic Study 5.4.8, FIS Study Report and Follow-up 5.4.10, Confidentiality 5.5.4, Notification to ERCOT Concerning Certain Project Developments 5.7.1, Generation Resource Data Requirements 5.7.2, Interconnection Study Fees 5.7.3, Stability Modeling Fee 5.7.4, Full Interconnection Study Fee/Cost 5.7.5, Interconnection Process Timetables Section 8, Attachment A: Declaration of Resource Data Accuracy Section 8, Attachment B: Declaration of Adequate Water Supplies |
| --- | --- |

Revised Proposed Guide Language

5.2.1	Generation Interconnection or Change Request Application

(1)	Any Entity seeking to interconnect a new All-Inclusive Generation Resource of ten MW or greater to the ERCOT System, upgrade the summer or winter Net Dependable Capability of an All-Inclusive Generation Resource by ten MW or greater within a single year, re-power an All-Inclusive Generation Resource of ten MW or greater, or change or add a Point of Interconnection (POI) of an All-Inclusive Generation Resource of ten MW or greater, as described in Section 5.1.1, Applicability, must submit the required Resource Registration data, in the format prescribed by ERCOT, available on the Market Information System (MIS) Public Area, and pay the applicable fees described in Section 5.7.2, Interconnection Study Fees.

(2)	All Generation Interconnection or Change Request (GINR) applications and supporting data submissions and required fees shall be submitted to ERCOT via the applicable generation interconnection process in the online GINR system.

(3)	The Interconnecting Entity (IE) shall provide in its GINR application all information necessary to allow for timely development, design, and implementation of any electric system improvements or enhancements required by ERCOT and the Transmission Service Provider (TSP) to reliably meet the interconnection requirements of the proposed Generation Resource.

(4)	ERCOT will return the GINR to the IE within ten days using the online GINR system if the GINR application fails to include the applicable fees or the information that is necessary to perform the initial screening interconnection studies.  The IE will be notified that action is required via a GINR automated email.

(5)	If the IE fails to respond to ERCOT’s inquiries within ten Business Days, the GINR will be deemed incomplete and returned to the IE using the online GINR system.  .  The IE will be notified that action is required via a GINR automated email.

(6)	Once the application has been deemed materially complete, ERCOT will notify the IE of receipt of the completed application using an online GINR system automated email within ten Business Days.  The IE should note that this acknowledgement is not a reservation of transmission capacity, either planned or unplanned.

(7)	An ERCOT designated point of contact will be assigned to oversee the interconnection study process and answer questions concerning the interconnection process.  Once assigned, the ERCOT designated point of contact will contact the IE and will be the primary ERCOT contact for the IE until the IE registers pursuant to paragraph (1) of Protocol Section 16.5, Registration of a Resource Entity.  At that time a Client Services Representative will be assigned and will be the designated point of contact.  If during the course of the studies, additional information is needed by ERCOT from the IE, ERCOT will return the GINR to the IE and the IE will have ten Business Days to answer the request for additional information by submitting a change request via the online GINR system without impacting the study timeline.  The IE will be notified that action is required via a GINR automated email.

(8)	Prior to the initial contact from the ERCOT designated point of contact, IEs should direct questions concerning the generation interconnection or change process to GINR@ercot.com.  All email communication sent to GINR@ercot.com shall include the associated project identification number (INR number) in the subject field.  If the communication is not specific to a project, the email subject field shall have the words “Generation Interconnection or Change Request.”

(9)	If proposed Generation Resources that would use the same physical transmission interconnection are to be built in stages with in-service dates more than one year apart, each stage should be treated as a separate interconnection request but may be included in the same study.

5.2.2	Generation Interconnection or Change Request Submission Requirements

(1)	In order to consider the GINR, a Security Screening Study Fee shall be submitted to ERCOT as part of the GINR application as prescribed in Section 5.2.1, Generation Interconnection or Change Request Application.  The Security Screening Study Fee is non-refundable.

(2)	ERCOT will assign a unique project identification number (INR number) to all GINRs according to the following convention:

yrINRxxxx

where:	yr is the calendar year the generation is anticipated to be online

INR indicates interconnection request

xxxx is a sequence number beginning with 0001 (reset for each year)

(3)	All correspondence relating to a specific GINR,  up to the commissioning of the All-Inclusive Generation Resource, shall reference the unique project identification number once it has been assigned by ERCOT.

5.3	Full Interconnection Study Request

(1)	Any Interconnecting Entity (IE) seeking a Full Interconnection Study (FIS) for interconnection to the ERCOT System must submit the following to ERCOT:

(a)	A change request via the online GINR system;

(b)	Resource Registration data in the format prescribed by ERCOT with applicable information required for interconnection studies identified in the Resource Registration Glossary;

(c)	A Stability Modeling Fee as prescribed in Section 5.7.3, Stability Modeling Fee;

(d)	Proof of site control as described in Section 5.4.9, Proof of Site Control; and

(e)	A declaration in Section 8, Attachment C, Declaration of Department of Defense Notification, certifying that:

(i)	The IE has notified the Department of Defense (DOD) Siting Clearinghouse of the proposed Generation Resource and requested an informal or formal review as described in 32 C.F.R. § 211.1 (2013); or

(ii)	The IE’s proposed Generation Resource is not required to provide notice to the DOD and Federal Aviation Administration (FAA) because the project does not meet the criteria requiring notice to the FAA under 14 C.F.R. § 77.9 (2010).

(2)	Transmission Service Providers (TSPs) may charge additional fees for their interconnection studies.

(3)	All FIS requests and supporting data submissions shall be entered via the online GINR system.

(4)	The ERCOT designated point of contact will initiate a FIS study scope meeting between the TSP(s) and the IE.  If during the course of the studies, additional information is needed by ERCOT from the IE, ERCOT will return the GINR to the IE and the IE will have ten Business Days to answer the request for additional information without impacting the study timeline.  The IE will be notified that action is required via a GINR automated email.

5.3.1	Full Interconnection Study Submission Requirements

(1)	When an FIS is requested, a Stability Modeling Fee must be submitted to ERCOT as prescribed by Section 5.7.3, Stability Modeling Fee.  The Stability Modeling Fee is non-refundable.  The IE must comply with the fee requirements before the FIS request can be submitted to ERCOT.  See Section 5.7.2, Interconnection Study Fees, for information regarding accepted methods of payment for fees.

(2)	All design data shall be submitted via the online GINR system.

(3)	The IE shall submit the Resource Registration data as specified in Section 5.7.1, Generation Resource Data Requirements, and as defined in the Resource Registration Glossary.

(4)	The Resource Registration data and all updates shall be submitted by the IE via the online GINR system.  This information will be used by ERCOT and the TSP(s) in the FIS.  The TSP may request additional information necessary to perform the FIS from the IE directly.  The IE must provide this information via the online GINR system in order to facilitate the completion of the FIS in a timely manner.

(5)	Resource Registration data required for the FIS shall accurately reflect the design of the facility.

5.3.2	Modifications to Request Declarations of Resource Data Accuracy

(1)	The IE shall maintain communication with ERCOT and the TSP at all stages of the generation interconnection process.  As soon as possible, but no later than ten Business Days after any relevant change, the IE shall submit a change request via the online GINR system to communicate any revisions that would affect the technical attributes and/or timeline of the project.  The TSP will receive a GINR system automated email when ERCOT reviews and acknowledges the change.

(2)	The IE shall update the Resource Registration data as soon as possible, but no later than ten Business Days, following any change to the proposed facility and shall submit the updated information via the online GINR system.  This obligation to update continues even after any interconnection agreement is signed.

(3)	Twice each year, each IE that has submitted an FIS request shall submit via the online GINR system, for each proposed facility, the declaration in Section 8, Attachment A, Declaration of Resource Data Accuracy, stating that, as of the date of submission, the most recently submitted data on the current version of the Resource Registration form accurately reflects the anticipated characteristics of the proposed Resource and that the contact information is correct.  The declaration shall be executed by an officer or other person having authority to bind the company and shall be submitted via the online GINR system.  Each IE shall submit one declaration for each project no earlier than March 1 and no later than March 15 each year, and shall submit another declaration for each proposed facility no earlier than September 1 and no later than September 15 each year.

(4)	If, after receipt of updated Resource Registration data, ERCOT or the TSP determines that any subsequent changes to the project may affect the reliable operation of the ERCOT System or otherwise warrant new studies, then ERCOT may require additional studies to be performed before the proposed Generation Resource is allowed to interconnect to the ERCOT System.  The IE and TSP(s) shall develop a schedule for completing the additional studies.  The TSP shall provide the FIS studies to ERCOT and the other TSPs via the online GINR system.  If these additional studies show that the project would not meet the operational standards specified in the Protocols, this Planning Guide, the Operating Guides, or Other Binding Documents, ERCOT may require the IE to demonstrate its compliance with these standards as a condition for energization of the proposed Generation Resource.

(5)	If the IE increases the requested amount of capacity of the proposed Generation Resource by more than 20% of the amount requested in the initial application, ERCOT shall require the IE to submit a new Generation Interconnection or Change Request (GINR) for the additional capacity or for the entire project.  ERCOT may, at its discretion, require the IE to submit a new GINR for significant capacity decreases or capacity increases of less than 20%, particularly if other changes to the request are also made, such as changes to the Commercial Operations Date.  ERCOT’s determination as to whether new studies are needed in no way affects the ongoing obligations of the IE and TSP to comply with North American Electric Reliability Corporation (NERC) Reliability Standards, Protocols, this Planning Guide and the Operating Guides.

(6)	Within ten Business Days, the IE shall notify ERCOT and the relevant TSP(s) of any change in ownership and shall provide conclusive documentary evidence of the ownership change (such as a purchase/sale agreement or a document executed by both parties confirming the transaction) via the online GINR system.  TSPs will receive a GINR system automated email when ERCOT reviews and acknowledges the change.

(7)	To support ERCOT resource adequacy and NERC reliability assessment reporting requirements, the IE shall enter into the online GINR system the following information for the proposed Generation Resource as soon as possible, but in no event later than ten Business Days after the information is available or has been updated:

(a)	Revisions to the initial projected Commercial Operations Date;

(b)	Notification if any required air permits have been issued or permit applications have been withdrawn; and

(c)	Notification and dates for when generator construction has commenced or been completed.

5.4.1	Security Screening Study

(1)	For each Generation Interconnection or Change Request (GINR), ERCOT will conduct a steady-state Security Screening Study, including power-flow and transfer studies, based on the expected in-service year to identify potential generation dispatch limitations based on the site proposed by the Interconnecting Entity (IE).  The Security Screening Study is a high level review of the project and generally includes a number of initial assumptions from both ERCOT and the IE.  In accordance with P.U.C. Subst. R. 25.198, Initiating Transmission Service, ERCOT will establish the scope of the Security Screening Study that will include a determination of the need for a more in-depth Subsynchronous Resonance (SSR) study.  The SSR vulnerability of all Generation Resources applicable under Section 5, Generation Resource Interconnection or Change Request, will be assessed pursuant to Protocol Section 3.22.1.2, Generation Resource Interconnection Assessment.

(2)	The results of the Security Screening Study will provide an indication of the level at which the proposed Generation Resource can expect to operate simultaneously with other known Generation Resources in the area before significant transmission additions or enhancements may be required.  During the course of the Security Screening Study, ERCOT may consult with the affected Transmission Service Provider(s) (TSP(s)), if needed, to identify the most efficient means of providing transmission service.

(3)	During the Security Screening Study phase of the GINR process, and in accordance with the Protocols, all data, documents, and other information required by ERCOT from an IE related to a request for GINR are considered Protected Information pursuant to Protocol Section 1.3.1.1, Items Considered Protected Information, to the extent that such information is not otherwise publicly available.  Accordingly, ERCOT shall not publicly release any of the protected data, documents, or other information during the Security Screening Study phase except to TSPs.  Information about GINRs in the Security Screening Study phase will only be released publicly in aggregated amounts.

(4)	Upon completion of the Security Screening Study, ERCOT will present the IE with a preliminary report indicating future transmission additions or enhancements that may be required to accommodate the proposed additional generation or Generation Resource modification at the specified in-service year.  This report will inform the IE about any additional transmission improvements estimated to be required for the continued security and reliability of the ERCOT System.  This report does not imply any commitment by ERCOT or any TSP to recommend or construct these transmission additions or enhancements.  The report will also contain a description of the SSR assessment performed as part of the Security Screening Study and any conclusions resulting from the SSR assessment.

(5)	Within 180 days of the date ERCOT notifies the IE of the Security Screening Study results, the IE must notify ERCOT, via the online GINR system, of its desire to pursue a Full Interconnection Study (FIS), otherwise ERCOT shall consider the GINR withdrawn by the IE.  ERCOT will begin initiation and coordination of the FIS only after receiving this Notification from the IE.  TSPs will receive a GINR system automated email when ERCOT determines the FIS application is complete.

(6)	After the expiration of the 180-day period, an IE must submit a new GINR for a Security Screening Study and must again pay the appropriate fee.  The IE will also be required to submit any updates or changes in the project’s data to ERCOT.

5.4.2.1	Full Interconnection Study Process Overview

(1)	Within ten Business Days of receiving notice to proceed with an FIS, proof of site control and the correct fee(s) from the IE, ERCOT will designate a TSP to lead the FIS and will contact that TSP to schedule an FIS scope meeting.  ERCOT will select the lead TSP based upon a preliminary analysis of the most likely Point of Interconnection (POI).  If an IE has previously developed a generation project in ERCOT with the selected TSP, the IE, ERCOT, and the TSP may agree to forgo the scope meeting.  If they so agree, the timeline for the IE and TSP to reach agreement on the FIS scope will start on the date ERCOT notifies the TSP of the IE’s decision to proceed with the FIS.

(2)	Notification of the FIS to all other TSP(s) will be provided via the online GINR system.  It is the responsibility of each TSP to determine if the proposed project would have a material impact on its Transmission Facilities and to decide whether and to what extent it should participate in the FIS.

(3)	Each TSP desiring to participate in the FIS shall promptly notify the lead TSP via email to the lead TSP.  The lead TSP must include all interested TSPs in the FIS to the extent such involvement is reasonable.

(4)	At the FIS scope meeting, the IE will present the proposed GINR and ERCOT will review the results of the Security Screening Study.  The lead TSP will facilitate a general discussion of the preliminary study scope of work for the FIS.

(5)	Pursuant to Protocol Section 3.22.1.2, Generation Resource Interconnection Assessment, in the event that the Security Screening Study performed by ERCOT identifies a possible SSR risk, ERCOT or the affected TSP(s) may require additional SSR studies be performed and may require an IE to provide additional detailed modeling data on the proposed Generation Resource in support of these studies.  The SSR studies shall be scoped at the same time as the FIS but do not need to be included as part of the FIS.

(6)	The IE and the TSP(s) must reach agreement on the FIS scope within 60 days of the FIS scope meeting.  The assistance of more than one TSP may be required in areas where Transmission Facilities are provided by multiple TSPs.  In these cases it may be necessary for the IE to execute study agreements with multiple TSPs.

(7)	The FIS scope agreement must include all assumptions, timetables, study cost estimates and payment schedules, and the determination of all requirements for interconnection.  The FIS must include all studies required by this section.  The IE and the TSP(s) shall consider the Security Screening Study and other preliminary studies and documents provided by the IE when developing the FIS scope.  The IE and TSP(s) may divide the FIS into distinct study phases, each requiring IE approval to proceed.

(8)	The TSP(s) shall submit the FIS scope document via the online GINR system.  The online GINR system will provide notification via an automated email to ERCOT and other TSP(s) of availability of the FIS scope document for review and comment.  Comments must be made within ten Business Days.

(9)	If the IE and TSP(s) cannot agree to the FIS study scope within the 60-day period, ERCOT will attempt to mediate an agreement.  If mediation is unsuccessful, ERCOT will consider whether the IE’s GINR should be terminated.  If the request is terminated, the IE will be required to file a new GINR and pay all appropriate fee(s) for any new generation project.

5.4.7	Economic Study

(1)	ERCOT shall perform an independent economic analysis of the transmission projects that are identified through this process as being needed for the direct connection of the proposed Generation Resource and that are expected to cost more than $25,000,000.  This economic analysis is performed only for informational purposes, and no ERCOT endorsement will be provided.

(2)	If the lead TSP determines that the costs of the recommended direct interconnection facilities for the proposed Generation Resource are expected to exceed $25,000,000, the lead TSP will submit a change request via the online GINR system to communicate this finding to ERCOT and other TSP(s) within ten Business Days of such determination.  This communication will include all available information upon which that finding is based, including but not limited to:

(a)	A description of the direct interconnection facilities;

(b)	Information necessary to modify a power-flow case to include those facilities;

(c)	Any information obtained from the IE that would be helpful in modeling the proposed Generation Resource for the study; and

(d)	The estimated cost of the facilities.

(3)	The IE shall provide to ERCOT any requested information necessary to accurately represent the Generation Resource in the economic study.

(4)	ERCOT will generally complete this economic study within 90 days, and will inform the TSP(s) and IE if additional time is required.  ERCOT will provide the results of the economic study to the IE and to the TSP(s) via the online GINR system.

5.4.8	FIS Study Report and Follow-up

(1)	The TSP(s) will submit a preliminary report of its findings and recommendations for each of the study elements as each is completed to ERCOT and to the other TSP(s) via the online GINR system.  Within ten Business Days of the TSP’s submission of a preliminary report to ERCOT and the other TSP(s), ERCOT will deliver a copy of each preliminary report to the IE via email and at the same time post a redacted copy of each preliminary report to the MIS Secure Area.

(2)	Any questions, comments, proposed revisions, or clarifications by any party shall be made in writing to the TSP(s) within ten Business Days after the issuance of each study report, which may cover one or more study elements.  ERCOT can extend this review period by an additional 20 Business Days in the online GINR system and an automated email will be sent to notify the affected TSP(s) and the IE that it needs additional time to review the report.

(3)	After considering the information received from ERCOT and other TSPs, the study element(s) report will be deemed complete and a final report shall be provided, via the online GINR system, to ERCOT and all TSPs.  The TSP(s) conducting the FIS shall submit via the online GINR system, the sub-synchronous oscillation analysis, if required, as a separate document from the remainder of the report.  The ten Business Day review period will be used by ERCOT to determine if any transmission upgrades proposed and clearly identified in the Steady-State Study Report need to be submitted to the RPG review process.  Protocol Section 3.11, Transmission Planning, provides more information on the process to review transmission upgrades that are unrelated to the direct connection of new or modified generation.

(4)	The final study element(s) report will be available via the online GINR system after the report has been deemed complete and marked “final”.  The final reports will be posted to the MIS Secure Area within 10 Business Days.  The IE can access the final reports via the online GINR System.

(5)	The study element(s) report shall not contain sensitive information including, but not limited to, confidential plant design information including stability study model data and parameters and contingencies causing instability.  The TSP(s) shall provide this information to ERCOT and other TSP(s) upon request.

(6)	The TSP issuing the final FIS element(s) report shall indicate that the report is the final report required by the FIS.  At the end of the ten Business Day review period following the issuance of the final FIS element(s) report, the FIS will be deemed complete and the IE and TSP may execute an SGIA.  If an economic study of the direct interconnection facilities is required, pursuant to Section 5.4.7, Economic Study, and has not yet been completed, the IE and TSP may agree that the completion of the economic study is not required before the FIS is deemed complete.

(7)	Should the IE wish to proceed with the proposed GINR, the IE must execute an SGIA with the respective TSP within 180 days following the completion of the FIS (includes all major study element(s) reports).

(8)	If during the time after the FIS is completed and before meeting the requirements of Section 6.9, Addition of Proposed Generation to the Planning Models,  changes occur that substantially differ from the assumptions used for the FIS, ERCOT and the TSP(s) shall determine the impact of the changes on the results of the FIS and, if applicable, SSR studies.  All changes shall be submitted to ERCOT through the Resource Registration process for a change comparison.  If the changes are determined by ERCOT to have the potential to materially alter the conclusions documented in the FIS, the TSP(s) will make appropriate modifications to the FIS.  The updated FIS reports will be submitted via the online GINR system.  Any questions, comments, proposed revisions, or clarifications by any party shall be made in writing to the TSP(s) within ten Business Days after the issuance of an updated study report.

5.4.10	Confidentiality

(1)	All data, documents or other information regarding the GINR, including the identity of the IE, will remain Protected Information until ERCOT receives written Notice from the IE that this information may be made public or until the IE requests an FIS.  Since the FIS scope agreement contains possibly confidential cost estimates and represents an agreement between the IE and the lead TSP, it will remain Protected Information and will not be released to parties other than those who are members of the confidential Transmission Owner Generation Interconnection list except as required in a court of law or by regulatory authorities having jurisdiction.  Once classified as a public project through one of these steps, ERCOT will make available via the online access the project description, all FIS reports, the results of the economic analysis of direct interconnection facilities costing over $25,000,000, and any information developed throughout the interconnection study process about transmission improvement projects that may be submitted for RPG review as a result of the new generation.

(2)	The lead TSP will notify the RPG email list via email within ten Business Days of the signing of an SGIA when the cost of the direct interconnection facilities is greater than $25,000,000.

5.5.4	Notification to ERCOT Concerning Certain Project Developments

(1)	The following submissions shall be provided to ERCOT via the online GINR system:

(a)	The TSP must submit a change request via the online GINR system within ten Business Days upon completion of the following events:

(i)	Signing of the FIS study scope agreement; and

(ii)	Funding of the FIS study scope agreement.

(b)	The TSP must submit a change request via the online GINR system to transmit a copy of the signed SGIA to ERCOT within ten Business Days of execution.

(c)	The TSP must submit a change request via the online GINR system within a ten Business Days of execution, a copy of any financially binding agreement between the IE and the TSP under which the interconnection for a Generation Resource will be constructed.

(d)	The TSP must submit a change request via the online GINR system within ten Business Days after it receives both a notice to proceed with construction of the interconnection for the Generation Resource and the financial security sufficient to fund the interconnection facilities pursuant to either agreement addressed in items (b) or (c) above.

(e)	A MOU or EC must submit a change request via the online GINR system confirming the Entity’s intent to construct and operate a proposed Generation Resource and interconnect such Generation Resource to its own transmission system.

(f)	Except for IEs proposing to interconnect Generation Resources powered by wind or photovoltaic solar energy, the IE must submit a change request via the online GINR system to provide Section 8, Attachment B, Declaration of Adequate Water Supplies, for each proposed Generation Resource within ten Business Days of securing the relevant water supply rights, or, for Resources that do not require a water supply right to operate (other than wind or photovoltaic solar), within ten Business Days of executing the SGIA.

5.7.1	Generation Resource Data Requirements

(1)	The Interconnecting Entity (IE) shall submit with its Generation Interconnection or Change Request (GINR) the most current actual facility information (generation, substation, and transmission/subtransmission if applicable) or best available expected performance data for the physical and electrical characteristics of all proposed facilities (in sufficient detail to provide a basis for modeling) up to the Point of Interconnection (POI) with a Transmission Service Provider (TSP).

(2)	Failure to supply the required data may delay ERCOT processing of the interconnection application and studies.  Recommendations resulting from these studies that are based on outdated, false, or bad data may adversely affect the safety and reliability of the ERCOT System and can result in damage to generation or transmission equipment.  The IE and subsequently, the Resource Entity associated with any approved Generation Resource, must promptly submit any updates to ERCOT to ensure the long-term adequacy, reliability, and safety of the ERCOT System, as required by the Protocols, this Planning Guide, the Operating Guides, and North American Electric Reliability Corporation (NERC) Reliability Standards.  Failure to comply may result in financial penalties.

(3)	In an effort to produce the best available Security Screening Study and Full Interconnection Study (FIS), ERCOT suggests that IEs begin collecting all appropriate engineering and equipment data from manufacturers as soon as the IE selects its major equipment for the proposed project.

(4)	While the duty to update data may require additional information, at a minimum, the IE shall submit the following data via the online GINR system at each step of the process:

- (a)	Application and Security Screening Study:

(i)	Generation Entity Information Sheet; and

(ii)	Generation Interconnection Screening Study Request Data.

- (b)	FIS:

(i)	Updates to the above information (if necessary);

(ii)	Applicable data required for interconnection studies as defined in the Resource Registration Glossary applicable to the Generation Resource type;

(iii)	Provision of the appropriate dynamic model for the proposed Generation Resource (some standard dynamic model forms are posted on the ERCOT website);

(iv)	If alternative models are required to appropriately represent the proposed Generation Resource, an alternative model may be provided by the IE, subject to verification by the lead TSP and ERCOT; and

(v)	In order to perform stability (transient and voltage) analyses, the IE shall provide unit stability model information and data to the TSP(s) and ERCOT via the online GINR system.  The Dynamics Working Group Procedural Manual contains more detail and IE dynamics data requirements.  Data submitted for transient stability models shall be compatible with ERCOT standard models (Siemens/PTI PSS/E and Powertech Labs Inc TSAT, VSAT and SSAT).  If no compatible model exists, the IE shall work with a consultant or software vendor to develop and supply accurate/appropriate models along with other associated data.  These models shall be incorporated into the standard model libraries of both software packages.  It is recommended that generation owners and developers encourage manufacturers and software vendors to work together to develop and maintain these important models.

- (c)	Prior to start of construction:

(i)	Any significant design changes in the generator(s) or main power transformer(s) of the proposed Generation Resource shall be provided to ERCOT and the TSP to ensure compatibility with the existing transmission system.

- (d)	Prior to the Resource Commissioning Date:

(i)	Registration and official Resource Registration data submittal pursuant to Section 6.8.2, Resource Registration Process;

(ii)	Updates to Resource Registration data based on “as-built” or “as-tested” data in all cases; and

(iii)	Proof of meeting ERCOT requirements (reactive, low Voltage Ride-Through (VRT) standards, stability models, Power System Stabilizer (PSS), Subsynchronous Resonance (SSR) models).

- (e)	During continuing operations:

(i)	The IE shall provide ERCOT and the TSP with any equipment data changes which result from equipment replacement, repair, or adjustment.  Unless otherwise required in the Protocols, this Planning Guide or the Operating Guides, the IE shall provide such data to ERCOT and the TSP no later than 60 days prior to the date of the actual change in equipment characteristics or during annual data update filings whichever occurs first.  This requirement shall also apply to all future owners throughout the service life of the project/plant.

5.7.2	Interconnection Study Fees

(1)	P.U.C. Subst. R. 25.198, Initiating Transmission Service, states in part that the customer requesting transmission service shall be responsible for all costs associated with the completion of the Security Screening Study and the FIS.

(2)	All fees payable to ERCOT shall be made via the online GINR system using Automated Clearing House (ACH) E-Checks or credit card.

5.7.3	Screening Study and Stability Modeling Fees

(1)	The ERCOT Security Screening Study fee is a non-refundable fee associated with each specific interconnection request.  The amount of this fee is listed in the ERCOT Fee Schedule of the Protocols.  The appropriate Security Screening Study fee must be remitted for each GINR (i.e. each individual interconnection location, Commercial Operations Date, and additional Generation Resource capacity at this specific interconnection location) at the time the application is submitted to ERCOT.

(2)	The ERCOT Stability Modeling Fee is a non-refundable fee based on the MW of additional installed capacity and is paid  when an FIS is requested.  The amount of this fee is listed in the ERCOT Fee Schedule of the Protocols.

(3)	This fee will reimburse ERCOT for the development of stability software models for each proposed Generation Resource and allow for continually updating current models as new equipment changes are made.

(4)	Payment of the Stability Modeling Fee to ERCOT does not release an IE from its obligation to provide ERCOT accurate and appropriate stability software models and data (including load data) for each of its proposed generation plants.

5.7.4	Full Interconnection Study Fee/Cost

(1)	The FIS fee/cost shall be paid directly to the TSP(s) completing the studies associated with the FIS by the IE.  The fee/cost will be agreed on and specified in the study scope agreement.  The TSP(s) shall directly invoice the IE for the reasonable costs associated with undertaking and completing the FIS.

(2)	ERCOT recommends that the Generation Resource and the TSP provide for a payment methodology and include a cancellation provision in the FIS scope agreement.

(3)	If the IE cancels the proposed Generation Resource via the online GINR system during the term of the FIS, the online GINR system will immediately notify ERCOT and  TSPs.

(4)	The IE is responsible for all costs associated with any work performed or non-cancelable commitments made prior to notifying ERCOT and the TSP(s) of the termination date of the project.  ERCOT highly recommends the TSP(s) receive the study fee before proceeding with work.

5.7.5	Interconnection Process Timetables

(1)	P.U.C. Subst. R. 25.198, Initiating Transmission Service, provides deadlines for ERCOT and TSP(s) to complete and report on the required interconnection studies provided that the IE submits all required data and appropriate fee(s).  Therefore, the IE must ensure that ERCOT and the TSP(s) performing these studies receive all required data in order to establish reasonable study models and assumptions that provide meaningful results and recommendations for interconnecting the proposed generating project.

(2)	Because the FIS is generally the critical path item in the GINR process, ERCOT recommends that a timetable for the FIS be developed and included in the study scope agreement.  In addition, major improvements to the transmission system resulting from interconnection requests should be identified as early in the process as possible so project validity can be considered before the parties go forward with extensive interconnection studies.  Once the FIS is underway, the parties may determine whether an adjustment to the original estimated completion date is necessary.  Should a schedule adjustment become necessary, the parties must provide Notice to ERCOT and the TSP(s) as soon as practicable, indicating the revised expected completion date.

(3)	The following timetable complies with P.U.C. Subst. R. 25.198.  It is intended to serve as a guideline only and the times stated are not requirements unless stated elsewhere in this section.  If the number of days shown is less than 30, these are Business Days; if the number of days shown is 30 days or more, these are calendar days.

| Task | Responsible Entity | Time Required to Complete |
| --- | --- | --- |
| Acknowledgement of GINR Application | ERCOT | 1 to 10 Business Days |
| Notification of Additional Information Needed to Complete Application | ERCOT | 1 to 10 Business Days |
| Perform Security Screening Study (after application is deemed complete) | ERCOT | 10 to 90 days |
| Decision to Pursue FIS (following issuance of Security Screening Study by ERCOT) | IE | Up to 180 days |
| Develop Scope Agreement for FIS (following IE’s Notification to ERCOT of desire for FIS and remittance of appropriate fees) | IE, ERCOT, and TSP(s) | Up to 60 days |
| Perform FIS (following agreement on scope) |  | 40 to 300 days |
| Steady-State and Transfer Analysis | TSP(s) | 10 to 90 days |
| System Protection Analysis (following Steady-State Analysis) | TSP(s) | 10 to 30 days |
| Dynamic and Transient Stability Analysis (following System Protection Study) | TSP(s) | 10 to 90 days |
| Facility Study | TSP(s) | 10 to 90 days |
| SSR | TSP(s) or IE | 90 days prior to Initial Synchronization |
| Study Report Review and Acceptance (following issuance of FIS) | ERCOT, and TSP(s) | 10 to 15 Business Days |
| FIS Posted to MIS | ERCOT | Within 10 days of being deemed complete |
| Report stability resolution findings to ERCOT | TSP | Within 90 days |
| Negotiate and Execute Standard Generation Interconnection Agreement (SGIA) (following acceptance of FIS) | IE and TSP | 180 days |

ERCOT Planning Guide

Section 8

Attachment A:  Declaration of Resource Data Accuracy

TBD

Declaration of Resource Data Accuracy

Name of Interconnecting Entity:

_____________________________________________________

Name and INR number of Project:

_____________________________________________________

Declaration Submission Period:

 March 1-15, 20___

 September 1-15, 20___

By signing below, I certify that I am knowledgeable about the design of the above-named project, and that the Resource registration form most recently submitted to ERCOT for the above-named project accurately reflects the anticipated characteristics of the proposed Resource and the project contact information in the online GINR system is correct.

I further certify that I am authorized to execute and submit this declaration on behalf of the Interconnecting Entity listed above, and that the statements contained herein are true and correct.

______________________________________

Signature

______________________________________

Name

______________________________________

Title

______________________________________

Date

ERCOT Planning Guide

Section 8

Attachment B:  Declaration of Adequate Water Supplies

TBD

Declaration of Adequate Water Supplies

An Interconnecting Entity (IE) must submit this attestation form to notify ERCOT that water rights, contracts or groundwater supplies sufficient for generation of electricity have been obtained or that water supplies are not required for the generation of electricity at each proposed Generation Resource.  Section 6.9, Addition of Proposed Generation to the Planning Models, requires an IE to submit this form before ERCOT may include certain proposed Generation Resources in the base cases created and maintained by the Steady State Working Group (SSWG), the System Protection Working Group (SPWG), and the Dynamics Working Group (DWG).  Any IE that proposes to interconnect a Generation Resource powered by wind, photovoltaic solar, or battery energy storage Resources does not need to submit this form.  However, any IE proposing to interconnect any other type of Generation Resource must submit this form, even if the IE’s proposed Resource will not use water.

Each IE should submit this attestation for each unique Generation Resource Interconnection Request (GINR) within ten Business Days of securing the relevant water supply rights, or, for Generation Resources that do not require water supplies to operate, within ten Business Days of executing the Interconnection Agreement with the TSP.  The attestation should be signed by an officer or other individual with authority to bind the IE.  The IE should submit the attestation and the necessary attachments to ERCOT via the online GINR system.

ATTESTATION

Name of Interconnecting Entity:

_____________________________________________________

Name and GINR Number of Project:

_____________________________________________________

By signing below, I certify that I am knowledgeable about the above-named project, and hereby represent as follows (check one of the following):

No water rights, contracts or groundwater supplies are needed for the above-named proposed Generation Resource to generate electricity.

The IE, the owner of the proposed Generation Resource, or another similarly situated party has secured water rights, contracts or groundwater supplies sufficient for the generation of electricity at the above-named proposed Generation Resource.  A copy of the relevant contract(s), permit(s) and/or groundwater adequacy studies is attached to this declaration.  The right(s) or contract(s) allows the Generation Resource owner or operator access to water according to the following terms (describe basic terms, including quantity, duration, and conditions of access):

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

______________________________________

Signature

______________________________________

Name

______________________________________

Title

______________________________________

Date