## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Chad Mulholland, NRG
ROS
July 17th, 2018

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    2 FMEs in the month of May
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 05/9/18
  NPRR863 – Separation of PFR and RRS Ancillary Service; Review by PDCWG Members on updated language to be discussed at next meeting
  NPRR872 – Modify the SASM Shadow Price CAP. NPRR wording clearly does not improve ERCOT reliability; however, whether there is a material decrease in reliability is difficult to ascertain.
  NERC Reliability Guideline: Generating Unit Operations During Complete Loss of Communications
  Regulation & Frequency Control Reports
  BAL-001-TRE-001
    ERCOT document for Operating Condition Guidelines for PFR Performance
    ERCOT preparing LCRA-Combined Cycle Steam Droop SAR
    ERCOT to determine Performance Evaluation to check for pass/fail before scoring and
    No Evaluation of Resources below LSL

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 2 FMEs in May
  5/5/2018 16:19:03
    Loss of 536 MW(IMFR=603MW/0.1Hz)
    Interconnection Frequency Response:
    7 of 43 Evaluated Generation Resources(1 of 24 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    9 of 43 Evaluated Generation Resources(3 of 24 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.
  5/21/2018 8:06:22
    Loss of 560 MW(IMFR=561MW/0.1Hz)
    Interconnection Frequency Response:
    5 of 24 Evaluated Generation Resources(1 of 24 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    5 of 24 Evaluated Generation Resources(1 of 24 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 943.16 MW/0.1Hz

## Slide 7: Frequency Control Report
May 2018

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections
There were no Time Error Corrections (TEC) in March

## Slide 12: ERCOT Total Energy

## Slide 13: ERCOT Total Energy from Wind Generation

## Slide 14: ERCOT % Energy from Wind Generation

## Slide 15
Questions?