## Slide 1
ERCOT Frequency Control Report
May 2018
ERCOT
Operations Planning
PDCWG | June 13th, 2018

## Slide 2: Frequency Control
CPS1, BAAL, & RMS1

## Slide 3: Hourly CPS1 by Day
May-18 CPS1 (%): 174.15
Notes: Outliers
5/29/18 12:00 – 16:00: Frequency continuously dragging due to wind ramping down. Wind ramped down roughly 2000MW over the course of 4 hours.
5/2/18 19:00: Frequency continuously dragging due to wind ramping down. Wind ramped down roughly 1200MW over the course of 25mins between 19:25 and 19:50.

## Slide 4: BAAL Exceedances & Violations
There were no BAAL exceedances

## Slide 5: 15-Minute Average CPS1%
May-18 CPS1 (%): 174.15

## Slide 6: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 176.99%

## Slide 7: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 14.4 mHz

## Slide 8: Daily RMS1 of ERCOT Frequency by Month

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 14.68 mHz
Min: 12.82 mHz
Max: 18.26 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events
UTC (t-0) |  | BA |  | BA | BA | Value "A" Information (MW) |  | Value "B" Information (MW) |  | SEFRD (FRM) |  | Exclude
Date / Time | Date/Time (t-0) | Time | B to A |  | Bias |  |  |  |  | for Bias | for R1 | for data
(MM/DD/YY HH:MM:SS) | BA Time | Zone | DelFreq | Time | DelFreq | Load Loss | Adjust | Load Loss | Adjust. | (MW/0.1Hz) | (MW/0.1Hz) | error *
2/5/2018 20:04:41 | 2/5/2018 14:04:41 | CST | -0.098 | 14:04:46 | -0.098 | 0.0 | 0.0 | 816.0 | 0.0 | -829.9 | -829.9 | N
2/14/2018 12:30:17 | 2/14/2018 06:30:17 | CST | -0.105 | 6:30:21 | -0.105 | 0.0 | 0.0 | 784.2 | 0.0 | -747.7 | -747.7 | N

## Slide 19: Op. Year 2018 BAL-003 FRM Performance
FRM Performance Results for 2018 | 
2018 | Current data year (December thru November)
-381.0 | Operating Year 2019 BA Frequency Response Obligation (FRO) for next year's FRM
-381.0 | Operating Year 2018 BA Frequency Response Obligation (FRO)
-788.77 | 2018 FRM - Median Estimated Frequency Response MW/0.1Hz for BA Compliance to R1, minimum Frequency Response
-788.8 | 2018 FRM - Average Estimated Frequency Response MW/0.1 Hz using SEFRD for R1
0.0 | 2018 FRM - Regression Estimated Frequency Response MW/0.1Hz using SEFRD for R1

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 33,819,614 Mwh

## Slide 22: Total Energy from Wind Generation
Notes: 7,071,468 MWh

## Slide 23: % Energy from Wind Generation
Notes: 20.91%

## Slide 24: ERCOT System Inertia

## Slide 25: Daily Minimum System Inertia
Notes: Minimum Inertia = 130,014 MW*s on 10/27/2017. This was also our record wind day.
May:
Mean: 218,229
Max: 273,032 on May 24th
Min: 159,027 on May 1st

## Slide 26: Questions?
Thank you!

## Slide 27: Op. Year 2017 BAL-003 Selected Events
Notes: Frequency Bias updated from 764 to 759 in April

## Slide 28: Op. Year 2017 BAL-003 FRM Performance
Notes: Put in some history of what these values were
Updated quarterly