## Slide 1
Update on the Investigation of Prices for the Real-Time on July 18 and Day-Ahead on July 20
Technical Advisory Committee Meeting
ERCOT Public
July 26, 2018

## Slide 2: Summary
Late last week, an issue was discovered with respect to the definition of two double-circuit contingencies.
The issue affected both the Day-Ahead and Real-Time Markets (DAM and RTM)
  Operating Day July 20, 2018 for the DAM
  Operating Day July 18, 2018 for the RTM
For the DAM, prices were corrected and published on July 23, 2018.
For the RTM, not able to correct and publish prices prior to the deadline of July 20, 2018 4:00 PM
  Will be seeking ERCOT Board of Directors approval of the price corrections at the August 7, 2018 meeting

## Slide 3: Contingency Definition Issue
The two contingencies impacted by this issue were DCNLHS8 and DLHSCNR8.
  Only DCNSLHS8 was part of a binding transmission constraint
  The constrained element in both markets was the 138 kV transmission line between Centerville Road and Lake Hubbard SES (3270__B)
These incorrect definitions resulted from a model change request to redefine the double-circuits involved and an ERCOT post-process tool error when creating the contingency definitions for the Energy and Market Management Systems (EMS and MMS)
  Congestion Revenue Rights (CRR) Auction models were not affected

## Slide 4: Contingency Definition Issue cont.
The process resulted in incorrect additional equipment being included in the two new contingency definitions.
The two contingency definitions were corrected for all models. Additional checks by the tool have been added to avoid similar concerns moving forward.
After analysis, no other contingencies were identified as being impacted by the issue.

## Slide 5: RTM and DAM Price Corrections
For the DAM, prices were corrected and published on July 23, 2018.
  Prior to the deadline of July 24, 2018 10:00 AM
For the RTM, not able to correct and publish prices prior to the deadline of July 20, 2018 4:00 PM
  Will be seeking ERCOT Board of Directors approval of the price corrections at the August 7, 2018 meeting

## Slide 6: Real-Time Pricing Impacts
Chart: Impact to the Hub Average Locational Marginal Prices for July 18, 2018
| 43299.68068287037 | 43299.68414351852 | 43299.687627314815 | 43299.691099537034 | 43299.694571759261 | 43299.69803240741 | 43299.701516203706 | 43299.704988425925 | 43299.708495370367 | 43299.711921296293 | 43299.71539351852 | 43299.718865740739 | 43299.722349537034 | 43299.725810185184 | 43299.72929398148 | 43299.732743055552 | 43299.736226851855 | 43299.739699074074 | 43299.740543981483 | 43299.741273148145 | 43299.74318287037 | 43299.746655092589 | 43299.750150462962 | 43299.753599537034 | 43299.757060185184 | 43299.76053240741 | 43299.764016203706 | 43299.767476851855
Calculated - Original | -6.391 | -6.4023 | -185.0001 | -29.7679 | -1.1274 | -1.7648 | -2.1443 | -1.4786 | -0.73033 | -0.030576 | -0.086042 | -0.029587 | -0.030506 | -0.034176 | -0.032766 | -0.33994 | -0.58172 | -0.044559 | -0.031223 | -0.72511 | -14.6921 | -0.31723 | -0.012014 | 0 | 0 | -0.030773 | 0 | -0.039244
Original | 1976.7629 | 1976.8852 | 1183.2046 | 158.0128 | 151.4063 | 132.021 | 130.3915 | 129.7305 | 76.1426 | 75.3988 | 75.4443 | 74.3357 | 75.4728 | 75.0054 | 74.2555 | 75.0204 | 74.088 | 75.4545 | 75.4981 | 150.9089 | 161.4725 | 74.9609 | 54.8609 | 44.7701 | 45.5103 | 46.7519 | 44.859 | 45.0335
Calculated | 1970.3718 | 1970.483 | 998.2045 | 128.2449 | 150.2789 | 130.2562 | 128.2472 | 128.2519 | 75.4123 | 75.3682 | 75.3583 | 74.3061 | 75.4423 | 74.9712 | 74.2227 | 74.6805 | 73.5062 | 75.41 | 75.4669 | 150.1838 | 146.7804 | 74.6437 | 54.8488 | 44.7701 | 45.5103 | 46.7211 | 44.859 | 44.9942
The Load Zone and Hubs were affected similarly.

## Slide 7: Real-Time Pricing Impacts cont.
Resource Node Locational Marginal Price Impact
for Interval 16:30 on July 18, 2018
Calculated – Original ($/MWh)
Prices most impacted were those near the constraint with the incorrect contingency.
The shadow prices for other transmission constraints also changed with the erroneous constraint removed.