## Slide 1
Re-power Timelines
John Bernecker
Supervisor, Resource Integration
7/31/18

## Slide 2: RARF Submittals
Updated RARFs should be submitted to ERCOT Resource Integration (via ProofPoint / RIOO) for initial GINR application and Planning Guide Section 6.9 compliance
Please do not submit RARFs via MIS until instructed to do so by ERCOT Resource Integration

## Slide 3: RARF Deadlines
RARFs for new units, if required for aggregation changes, must be approved by ERCOT 90 days prior to the first of the month of the MRD
  ERCOT requires at least 30 days for approval of aggregation requests (~120 prior to the MRD)
RARFs not requiring new units may be submitted via Interim Update Request
  Interim Update Requests are not guaranteed to be approved by ERCOT Network Modeling
ERCOT recommends that all RARF submittals follow the 90-day rule

## Slide 4: New Generator Commissioning Checklist
Commissioning Plan, Part 2 checklist, and Part 3 checklist are required for re-powers
Part 2 checklist has been modified for re-powers
  Part 2a approval is required prior to starting any re-power work
  Part 2b approval is required following the completion of re-power work and the Model Ready Date for the re-powered site
Part 3 checklist is identical to that for new units
  Unit tests are required prior to Part 3 approval

## Slide 5: Part 2a
Part 2a approval is required prior to starting any re-power work
The following items must be complete prior to Part 2a approval
  Specific Protocol Compliance Check items
  RARFs detailing aggregation requests submitted
  FIS approved by ERCOT
  Reactive Study approved by ERCOT

## Slide 6: Part 2b
Part 2b approval is required following the completion of re-power work and the Model Ready Date for the re-powered site
The following items must be complete prior to Part 2b approval
  All Protocol Compliance Check items
  Re-powered site and any required GTC are in the Network Operations Model
  All telemetry is in place and functioning properly
  SSR study, if required, has been approved for at least 90 days

## Slide 7: Modeling and Commissioning Timeline