| NPRR Number | 879 | NPRR Title | SCED Base Point and Performance Evaluation Changes for IRRs that Carry Ancillary Services |
| --- | --- | --- | --- |
| Date |  | August 3, 2018 |  |
| Submitter’s Information |  |  |  |
| Name |  | Sandip Sharma / Nitika Mago / Austin Rosel |  |
| E-mail Address |  | Sandip.Sharma@ercot.com / Nitika.Mago@ercot.com / Austin.Rosel@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-4298 / 512-248-6601 / 512-248-6686 |  |
| Cell Number |  |  |  |
| Market Segment |  | Not applicable |  |

Comments

ERCOT submits these comments in order to maintain alignment between the GREDP and the Base Point Deviation charges for Intermittent Renewable Resources (IRRs) carrying Ancillary Service Resource Responsibilities.  Also included is language to clarify that all IRRs within an IRR Group will receive a Security-Constrained Economic Dispatch (SCED) Base Point calculated using the five-minute intra-hour forecast of the Resource when one or more IRRs within the IRR Group are carrying Ancillary Service Resource Responsibilities.

Additionally, ERCOT has received interest from some Market Participants to send IRR-specific 5-mins out High Sustained Limit (HSL) telemetry to ERCOT.  ERCOT systems will compute SCED Base Points for IRRs when carrying Ancillary Service Resource Responsibility using the 5-mins out HSL telemetry when available, if no such telemetry is available ERCOT will use the five-minute intra-hour forecast of the Resource available in ERCOT systems.

Revised Cover Page Language

| NPRR Number | 879 | NPRR Title | SCED Base Point, Base Point Deviation, and Performance Evaluation Changes for IRRs that Carry Ancillary Services |
| --- | --- | --- | --- |
| Nodal Protocol Sections Requiring Revision |  | 6.5.7.2, Resource Limit Calculator 6.6.5.1.1.1, Base Point Deviation Charge for Over Generation 6.6.5.1.1.2, Base Point Deviation Charge for Under Generation 6.6.5.1.1.3, Controllable Load Resource Base Point Deviation Charge for Over Consumption 6.6.5.1.1.4, Controllable Load Resource Base Point Deviation Charge for Under Consumption 6.6.5.2, IRR Generation Resource Base Point Deviation Charge 8.1.1.4.1, Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) proposes that Intermittent Renewable Resources (IRRs) carrying Ancillary Service Resource Responsibilities receive a Security-Constrained Economic Dispatch (SCED) Base Point calculated using the five-minute intra-hour forecast of the Resource. Generation Resource Energy Deployment Performance (GREDP) metrics are added to score performance during these intervals. Base Point Deviation Charges are adjusted to treat IRRs providing Ancillary Services the same as conventional generators. These changes cannot be done manually and will be active once a system change is implemented. This NPRR contains clean-up changes to correct the unit of measure for some billing determinants, and an as-built correction to the Settlement equation in paragraph (4) of Section 6.6.5.2. These clean-up changes do not introduce any system impact or Settlement changes. This NPRR also contains administrative edits to paragraphs (7) - (9) of Section 8.1.1.4.1, to align the paragraph numbering with current Protocol formatting style. These edits are authored as “ERCOT Market Rules” in this NPRR. |  |
| Business Case |  | Currently, the ERCOT Protocols do not specify performance criteria or Base Point Deviation charges for IRRs carrying Ancillary Service Resource Responsibilities. IRRs have recently qualified to provide Ancillary Services and in the absence of this NPRR, ERCOT will have to manually perform analysis to measure their performance, which is a process that can be inefficient and susceptible to errors. IRRs currently are only required to meet GREDP metrics and Base Point Deviation criteria when curtailed. To correctly score the performance of an IRR carrying Ancillary Service Resource Responsibilities, through this NPRR, these Resources will receive a SCED Base Point calculated using the five-minute intra-hour forecast of the Resource. The Resource will then be required to meet GREDP performance metrics for these intervals. |  |

Revised Proposed Protocol Language

6.5.7.2	Resource Limit Calculator

(1)	ERCOT shall calculate the HASL, LASL, SURAMP, SDRAMP, HDL and LDL within four seconds after a change of the Resource-specific attributes provided as part of the QSE’s SCADA telemetry under Section 6.5.5.2, Operational Data Requirements.  The formulas described below define which Resource-specific attributes must be used to calculate each Resource limit.  The Resource limits are used as inputs into both the SCED process and the Ancillary Service Capacity Monitor as described in Section 6.5.7.6, Load Frequency Control.  These Resource limits help ensure that the deployments produced by the SCED and Load Frequency Control (LFC) processes will respect the commitment of a Resource to provide Ancillary Services as well as individual Resource physical limitations.

(2)	The figures below illustrate how the Resource Limit Calculator determines the Resource limits for Generation and Load Resources:

Generation Resources:

LSL

HSL

Time

LSL

-

LASL

-

HASL

-

Generation

Increase

Generation

Decrease

Services

Provided: Reg

Down

Provided: Reg Up,

Responsive, Non-Spin

Current

Telemetry

HDL

LDL

Ramp

Rate

5 Minutes

Generation

Quantity

Offer Curve Generation

LSL

HSL

-

-

-

Generation

Increase

Generation

Decrease

Ramp

Rate

5 Minutes

-

0

-

-

Generation

Increase

Generation

Decrease

Ramp

Rate

5 Minutes

Ancillary

Load Resources:

Time

LSL = LPC -

LASL  -

HASL  -

Ancillary Services Provided: Reg-Down

Current Load

Telemetry

HDL

LDL

5-30 Minutes

Load

Quantity

Bid Curve Load

LSL/LPC

HSL/MPC

0

Increasing

Consumption

Decreasing

Consumption

Ramp

Rate

Ancillary Services Provided: Reg-Up, RRS, Non-Spin

HSL = MPC -

Normal Load

Fluctuation

(3)	For Generation Resources, HASL is calculated as follows:

HASL	=	Max (LASL, (HSLTELEM – (RRSTELEM + RUSTELEM + NSRSTELEM +NFRCTELEM)))

| Variable | Description |
| --- | --- |
| HASL | High Ancillary Service Limit. |
| HSLTELEM | For IRRs carrying Ancillary Service Resource Responsibilities and all IRRs within an IRR Group where any IRR within the IRR Group is carrying an Ancillary Service Resource Responsibility, HSLTELEM shall be the five-minute intra-hour forecast for the Resource. For all other Resources, HSLTELEM shall be the Resource’s HSL provided to ERCOT via telemetry, in accordance with Section 6.5.5.2. |
| LASL | Low Ancillary Service Limit. |
| RRSTELEM | Responsive Reserve Ancillary Service Schedule provided by telemetry. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| NSRSTELEM | Non-Spin Ancillary Service Schedule provided via telemetry. |
| NFRCTELEM | NFRC currently available (unloaded) and included in the HSL of the Generation Resource with non-zero Responsive Reserve Ancillary Service Schedule telemetry. |

(4)	For Generation Resources, LASL is calculated as follows:

LASL	=	LSLTELEM + RDSTELEM

| Variable | Description |
| --- | --- |
| LASL | Low Ancillary Service Limit. |
| LSLTELEM | Low Sustained Limit provided via telemetry. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation provided by telemetry. |

(5)	For each Generation Resource, the SURAMP is calculated as follows:

SURAMP	=	RAMPRATE – (RUSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SURAMP | SCED Up Ramp Rate. |
| RAMPRATE | Normal Ramp Rate up, as telemetered by the QSE, when RRS is not deployed or when the subject Resource is not providing RRS. Emergency Ramp Rate up, as telemetered by the QSE, for Resources deploying RRS. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(6)	For each Generation Resource, the SDRAMP is calculated as follows:

SDRAMP	=	NORMRAMP – (RDSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SDRAMP | SCED Down Ramp Rate. |
| NORMRAMP | Normal Ramp Rate down, as telemetered by the QSE. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation by Resource provided via telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(7)	For Generation Resources, HDL is calculated as follows:

(a)	If the telemetered Resource Status is SHUTDOWN, then

HDL	=	POWERTELEM – (SDRAMP * 5)

(b)	If the telemetered Resource Status is any status code specified in item (5)(b)(i) of Section 3.9.1, Current Operating Plan (COP) Criteria, other than SHUTDOWN, then

HDL	=	Min (POWERTELEM + (SURAMP * 5), HASL)

| Variable | Description |
| --- | --- |
| HDL | High Dispatch Limit. |
| POWERTELEM | Gross or net real power provided via telemetry. |
| SURAMP | SCED Up Ramp Rate. |
| SDRAMP | SCED Down Ramp Rate. |
| HASL | High Ancillary Service Limit – definition provided in Section 2, Definitions and Acronyms. |

(8)	For Generation Resources, LDL is calculated as follows:

(a)	If the telemetered Resource Status is STARTUP, then

LDL	=	POWERTELEM + (SURAMP * 5)

(b)	If the telemetered Resource Status is any status code specified in item (5)(b)(i) of Section 3.9.1 other than STARTUP, then

LDL	=	Max (POWERTELEM - (SDRAMP * 5), LASL)

| Variable | Description |
| --- | --- |
| LDL | Low Dispatch Limit. |
| POWERTELEM | Gross or net real power provided via telemetry. |
| SDRAMP | SCED Down Ramp Rate. |
| LASL | Low Ancillary Service Limit – definition provided in Section 2. |

(9)	For Load Resources, HASL is calculated as follows:

HASL	=	Max (LPCTELEM, (MPCTELEM – RDSTELEM))

| Variable | Description |
| --- | --- |
| HASL | High Ancillary Service Limit. |
| LPCTELEM | Low Power Consumption provided via telemetry. |
| MPCTELEM | Maximum Power Consumption provided via telemetry. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation provided by telemetry. |

(10)	For Load Resources, LASL is calculated as follows:

LASL	=	Min (HASL, (LPCTELEM + (RRSTELEM + RUSTELEM + NSRSTELEM)))

| Variable | Description |
| --- | --- |
| LASL | Low Ancillary Service Limit. |
| HASL | High Ancillary Service Limit. |
| LPCTELEM | Low Power Consumption provided via telemetry. |
| RRSTELEM | Responsive Reserve Ancillary Service Schedule provided by telemetry. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| NSRSTELEM | Non-Spin Ancillary Service Schedule provided via telemetry. |

(11)	For each Load Resource, the SURAMP is calculated as follows:

SURAMP	=	RAMPRATE – (RUSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SURAMP | SCED Up Ramp Rate. |
| RAMPRATE | Normal Ramp Rate up, as telemetered by the QSE, when RRS is not deployed or when the subject Load Resource is not providing RRS. Emergency Ramp Rate up, as telemetered by the QSE, for Load Resources deploying RRS. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(12)	For each Load Resource, the SDRAMP is calculated as follows:

SDRAMP	=	NORMRAMP – (RDSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SDRAMP | SCED Down Ramp Rate. |
| NORMRAMP | Normal Ramp Rate down, as telemetered by the QSE. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation by Resource provided via telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(13)	For Load Resources, HDL is calculated as follows:

HDL	=	Min (POWERTELEM + (SDRAMP * 5), HASL)

| Variable | Description |
| --- | --- |
| HDL | High Dispatch Limit. |
| POWERTELEM | Net real power flow provided via telemetry. |
| SDRAMP | SCED Down Ramp Rate. |
| HASL | High Ancillary Service Limit – definition provided in Section 2. |

(14)	For Load Resources, LDL is calculated as follows:

LDL	=	Max (POWERTELEM - (SURAMP * 5), LASL)

| Variable | Description |
| --- | --- |
| LDL | Low Dispatch Limit. |
| POWERTELEM | Net real power flow provided via telemetry. |
| SURAMP | SCED Up Ramp Rate. |
| LASL | Low Ancillary Service Limit – definition provided in Section 2. |

- 6.6.5.1.1.1	Base Point Deviation Charge for Over Generation

(1)	ERCOT shall charge a QSE for a Generation Resource, including an IRR carrying an Ancillary Service Resource Responsibility for at least one SCED interval within the 15-minute Settlement Interval, for over-generation that exceeds the following tolerance.  The tolerance is the greater of:

(a)	5% of the average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments; or

(b)	Five MW for metered generation above the average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments.

(2)	For instances in which an IRR is not carrying an Ancillary Service Resource Responsibility or is part of an IRR Group in which no IRR is carrying an Ancillary Service Resource Responsibility for at least one SCED interval within the 15-minute Settlement Interval, Base Point Deviation Charges will be determined per Section 6.6.5.2, IRR Generation Resource Base Point Deviation Charge.

(3)	The over-generation charge to each QSE for each Generation Resource, that is not an IRR, at each Resource Node Settlement Point is calculated as follows:

BPDAMT q, r, p, i 	=	Max (PR1, RTSPP p, i) * OGEN q, r, p, i

Where:

OGEN q, r, p, i  = Max [0, (TWTGq, r, p, i  – ¼ * Max (((1 + K1) * AABP q, r, p, i), (AABP q, r, p, i + Q1)))]

TWTG q, r, p, i	=	( (AVGTG5M q, r, p, i, y) / 3) * ¼

(4)	If any IRR in an IRR Group is carrying an Ancillary Service Resource Responsibility for at least one SCED interval within the 15-minute Settlement Interval, then the deviation penalty is determined for the IRR Group and evenly allocated and charged to each IRR within that IRR Group as follows:

BPDAMT q, r, p, i        =      Max (PR1, RTSPP p, i) * OGEN q, r, p, i

Where:

OGEN q, r, p, i  = Max [0, (TWTGq, wg, p, i  – ¼ * Max (((1 + K1) * AABP q, wg, p, i),

(AABP q, wg, p, i + Q1)))] / N

TWTG q, wg, p, i	=  (Σy (AVGTG5M q, r, p, i, y) / 3) * ¼

AABP q, wg, p, i  = (AABP q,r, p, i)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BPDAMT q, r, p, i | $ | Base Point Deviation Charge per QSE per Settlement Point per Resource—The charge to QSE q for Generation Resource r at Resource Node p, for its deviation from Base Point, for the 15-minute Settlement Interval i. The Base Point Deviation Charge is charged to the Combined Cycle Train for all Combined Cycle Generation Resources. |
| RTSPP p, i | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval i. |
| TWTG q, r, p, i | MWh | Time-Weighted Telemetered Generation per QSE per Settlement Point per Resource—The telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval i. Where for a Combined Cycle Train, the Resource r is the Combined Cycle Train. |
| AABP q, r, p, i | MW | Adjusted Aggregated Base Point per QSE per Settlement Point per Resource—The aggregated Base Point adjusted for Ancillary Service deployments, of Generation Resource or Controllable Load Resource r represented by QSE q at Settlement Point p, for the 15-minute Settlement Interval i. Where for a Combined Cycle Train, AABP is calculated for the Combined Cycle Train considering all SCED Dispatch Instructions to any Combined Cycle Generation Resources within the Combined Cycle Train. |
| AVGTG5M q, r, p, i, y | MW | Average Telemetered Generation for the 5 Minutes—The average telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the five-minute clock interval y, within the 15-minute Settlement Interval i. |
| OGEN q, r, p, i | MWh | Over Generation Volumes per QSE per Settlement Point per Resource—The amount over-generated by the Generation Resource r represented by QSE q at Resource Node p for the 15- minute Settlement Interval i. |
| PR1 | $/MWh | The price to use for the Base Point Deviation Charge for over-generation when RTSPP is less than $20/MWh, $20/MWh. |
| K1 | none | The percentage tolerance for over-generation, 5%. |
| Q1 | MW | The MW tolerance for over-generation, five MW. |
| N | none | The number of IRRs within an IRR Group. |
| q | none | A QSE. |
| p | none | A Settlement Point. |
| r | none | A non-exempt Resource. |
| y | none | A five-minute clock interval in the Settlement Interval. |
| i | none | A 15-minute Settlement Interval. |
| wg | none | An IRR Group. |

- 6.6.5.1.1.2	Base Point Deviation Charge for Under Generation

(1)	ERCOT shall charge a QSE for a Generation Resource, including an IRR carrying an Ancillary Service Resource Responsibility for at least one SCED interval within the 15-minute Settlement Interval, for under generation if the metered generation is below the lesser of:

(a)	95% of the average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments; or

(b)	The average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments minus five MW.

(2)	For instances in which an IRR is not carrying Ancillary Service Resource Responsibility or is part of an IRR Group in which no IRR is carrying an Ancillary Service Resource Responsibility for at least one SCED interval within the 15-minute Settlement Interval, Base Point Deviation Charges will be determined per Section 6.6.5.2, IRR Generation Resource Base Point Deviation Charge.

(3)	The under-generation charge to each QSE for each Generation Resource, that is not an IRR, at each Resource Node Settlement Point for a given 15-minute Settlement Interval is calculated as follows:

BPDAMT q, r, p, i	=	-1 * Min (PR2, RTSPPp,i) * Min (1, KP) * UGEN q, r, p, i

Where:

UGEN q, r, p, i  =  Max [0, [Min ((1 - K2) * ¼* AABP q, r, p, i ,

¼ * (AABP q, r, p, i  - Q2)) - TWTGq, r, p, i]]

TWTG q, r, p, i	=	( (AVGTG5M q, r, p, i, y) / 3) * ¼

(4)	If any IRR in an IRR Group is carrying an Ancillary Service Resource Responsibility for at least one SCED interval within the 15-minute Settlement Interval, then the deviation penalty is determined for the IRR Group and evenly allocated and charged to each IRR within that IRR Group as follows:

BPDAMT q, r, p, i      =	-1 * Min (PR2, RTSPP p, i) * Min (1, KP) * UGEN q, r, p, i

Where:

UGEN q, r, p, i     = 	Max [0, [Min ((1 - K2) * ¼* AABP q, wg, p, i ,

¼ * (AABP q, wg, p, i  - Q2)) - TWTGq, wg, p, i]] / N

TWTG q, wg, p, i	  =	 (Σy (AVGTG5M q, r, p, i, y) / 3) * ¼

AABP q, wg, p, i       = 	(AABP q, r, p, i)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BPDAMT q, r, p, i | $ | Base Point Deviation Charge per QSE per Settlement Point per Resource—The charge to QSE q for Generation Resource r at Resource Node p, for its deviation from Base Point, for the 15-minute Settlement Interval i. A Base Point Deviation Charge is charged to the Combined Cycle Train for all Combined Cycle Generation Resources. |
| RTSPP p, i | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval i. |
| TWTG q, r, p, i | MWh | Time-Weighted Telemetered Generation per QSE per Settlement Point per Resource—The telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval i. Where for a Combined Cycle Train, the Resource r is the Combined Cycle Train. |
| AABP q, r, p, i | MW | Adjusted Aggregated Base Point—The aggregated Base Point adjusted for Ancillary Service deployments of Generation Resource or Controllable Load Resource r represented by QSE q at Settlement Point p, for the 15-minute Settlement Interval i. Where for a Combined Cycle Train, AABP is calculated for the Combined Cycle Train considering all SCED Dispatch Instructions to any Combined Cycle Generation Resources within the Combined Cycle Train. |
| AVGTG5M q, r, p, i, y | MW | Average Telemetered Generation for the 5 Minutes —The average telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the five-minute clock interval y, within the 15-minute Settlement Interval i. |
| UGEN q, r, p, i | MWh | Under Generation Volumes per QSE per Settlement Point per Resource—The amount under-generated by the Generation Resource r represented by QSE q at Resource Node p for the 15-minute Settlement Interval i. |
| KP | None | The coefficient applied to the Settlement Point Price for under-generation charge, 1.0. |
| PR2 | $/MWh | The price to use for the Base Point Deviation Charge for under-generation calculation when RTSPP is greater than -$20/MWh, -$20/MWh. |
| K2 | None | The percentage tolerance for under-generation, 5%. |
| Q2 | MW | The MW tolerance for under-generation, five MW. |
| N | none | The number of IRRs within an IRR Group. |
| q | none | A QSE. |
| p | none | A Settlement Point. |
| r | none | A non-exempt Resource. |
| y | none | A five-minute clock interval in the Settlement Interval. |
| i | none | A 15-minute Settlement Interval. |
| wg | none | An IRR Group. |

- 6.6.5.1.1.3	Controllable Load Resource Base Point Deviation Charge for Over Consumption

(1)	ERCOT shall charge a QSE for a Controllable Load Resource for over-consumption that exceeds the following tolerance.  The tolerance is the greater of:

(a)	XO% of the average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments; or

(b)	YO MW for power consumption above the average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments.

(2)	The Controllable Load Resource Base Point Deviation Charge for over-consumption variables XO and YO shall be subject to review and approval by the Technical Advisory Committee (TAC) and shall be posted to the MIS Public Area no later than three Business Days after TAC approval.

(3)	The charge to each QSE for non-excused over-consumption for each Controllable Load Resource during a 15-minute Settlement Interval in which the Controllable Load Resource has received a Base Point is calculated as follows:

BPDAMT q, r, p, i =	-1 * Min (PRZ1, RTSPPp,i) * Min (1, KP1) * OCONSM q, r, p, i

Where:

OCONSM q, r, p, i   = Max [0, (ATPCq, r, p, i  - ¼* Max (((1 + KLR1) * AABP q, r, p, i), (AABP q, r, p, i + QLR1)))]

ATPC q, r, p, i	=       ( (AVGTPC5M q, r, p i ,y) / 3) * ¼

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BPDAMT q, r, p, i | $ | Base Point Deviation Charge per QSE per Settlement Point per Resource—The charge to QSE q for Generation Resource or Controllable Load Resource r at Settlement Point p, for its deviation from Base Point, for the 15-minute Settlement Interval i. |
| RTSPP p, i | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval i. |
| ATPC q, r, p, i | MWh | Average Telemetered Power Consumption per QSE per Settlement Point per Controllable Load Resource—The average telemetered power consumption of the Controllable Load Resource r represented by QSE q at Settlement Point p, for the 15-minute Settlement Interval i. |
| AABP q, r, p, i | MW | Adjusted Aggregated Base Point per QSE per Settlement Point per Resource—The aggregated Base Point adjusted for Ancillary Service deployments of Generation Resource or Controllable Load Resource r represented by QSE q at Settlement Point p, for the 15-minute Settlement Interval i. |
| AVGTPC5M q, r, p, i, y | MW | Average Telemetered Power Consumption for the 5 Minutes—The average telemetered power consumption of Controllable Load Resource r represented by QSE q at Settlement Point p, for the five-minute clock interval y, within the 15-minute Settlement Interval i. |
| OCONSM q, r, p, i | MWh | Over-Consumption Volumes per QSE per Settlement Point per Controllable Load Resource—The amount over-consumed by the Controllable Load Resource r represented by QSE q at Settlement Point p for the 15-minute Settlement Interval i. |
| KP1 | none | The coefficient applied to the Settlement Point Price for over-consumption charge, 1.0. |
| PRZ1 | $/MWh | The price to use for the charge calculation when RTSPP is greater than -$20, -$20/MWh. |
| KLR1 | none | The percentage tolerance for over-consumption of a Controllable Load Resource, XO%. |
| QLR1 | MW | The MW tolerance for over-consumption of a Controllable Load Resource, YO MW. |
| q | none | A QSE. |
| p | none | A Settlement Point. |
| r | none | A Controllable Load Resource. |
| i | none | A 15-minute Settlement Interval. |
| y | none | A five-minute clock interval in the Settlement Interval. |

- 6.6.5.1.1.4	Controllable Load Resource Base Point Deviation Charge for Under Consumption

(1)	ERCOT shall charge a QSE for a Controllable Load Resource for under-consumption if the average telemetered power consumption is below than the lesser of:

(a)	[100-XU]% of the average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments; or

(b)	The average of the Base Points in the Settlement Interval adjusted for any Ancillary Service deployments minus YU MW.

(2)	The Controllable Load Resource Base Point Deviation Charge for under-consumption variables XU and YU shall be subject to review and approval by TAC and shall be posted to the MIS Public Area no later than three Business Days after TAC approval.

(3)	The charge to each QSE for non-excused under-consumption of each Controllable Load Resource during a 15-minute Settlement Interval in which the Controllable Load Resource has received a Base Point is calculated as follows:

BPDAMT q, r, p, i =	Max (PRZ2, RTSPP p, i) * UCONSM q, r, p, i

Where:

UCONSM q, r, p, i   = Max [0, [Min ((1 – KLR2) * ¼* AABP q, r, p, i , ¼ * (AABP q, r, p, i – QLR2)) – ATPCq, r, p, i]]

ATPC q, r, p, i	=       ( (AVGTPC5M q, r, p i ,y,) / 3) * ¼

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BPDAMT q, r, p, i | $ | Base Point Deviation Charge per QSE per Settlement Point per Resource—The charge to QSE q for Generation Resource or Controllable Load Resource r at Settlement Point p, for its deviation from Base Point, for the 15-minute Settlement Interval i. |
| RTSPP p, i | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Settlement Point p, for the 15-minute Settlement Interval i. |
| ATPC q, r, p, i | MWh | Average Telemetered Power Consumption per QSE per Settlement Point per Controllable Load Resource—The average telemetered power consumption of the Controllable Load Resource r represented by QSE q at Settlement Point p, for the 15-minute Settlement Interval i. |
| AABP q, r, p, i | MW | Adjusted Aggregated Base Point per QSE per Settlement Point per Resource—The aggregated Base Point adjusted for Ancillary Service deployments of Generation Resource or Controllable Load Resource r represented by QSE q at Settlement Point p, for the 15-minute Settlement Interval i. |
| AVGTPC5M q, r, p, i, y | MW | Average Telemetered Power Consumption for the 5 Minutes—The average telemetered power consumption of Controllable Load Resource r represented by QSE q at Settlement Point p, for the five-minute clock interval y, within the 15-minute Settlement Interval i. |
| UCONSM q, r, p, i | MWh | Under Consumption Volumes per QSE per Settlement Point per Controllable Load Resource—The amount under-consumed by the Controllable Load Resource r represented by QSE q at Settlement Point p for the 15-minute Settlement Interval i. |
| PRZ2 | $/MWh | The price to use for the Base Point Deviation Charge for under-consumption calculation when RTSPP is less than $20/MWh, $20/MWh. |
| KLR2 | none | The percentage tolerance for under-consumption of a Controllable Load Resource, XU%. |
| QLR2 | MW | The MW tolerance for under-consumption of a Controllable Load Resource, YU MW. |
| q | none | A QSE. |
| p | none | A Settlement Point. |
| r | none | A Controllable Load Resource. |
| i | none | A 15-minute Settlement Interval. |
| y | none | A five-minute clock interval in the Settlement Interval. |

- 6.6.5.2	IRR Generation Resource Base Point Deviation Charge

(1)	ERCOT shall charge a QSE for an IRR a Base Point Deviation Charge if the IRR metered generation is more than 10% above its Adjusted Aggregated Base Point, the flag signifying that the IRR has received a Base Point below the High Dispatch Limit (HDL) used by SCED has been received, and the IRR is not carrying an Ancillary Service Resource Responsibility and is not part of an IRR Group in which at least one IRR is carrying an Ancillary Service Resource Responsibility for at least one SCED interval within the 15-minute Settlement Interval.

(2)	For instances in which an IRR is carrying an Ancillary Service Resource Responsibility or is part of an IRR Group in which at least one IRR is carrying an Ancillary Service Resource Responsibility for at least one SCED interval within the 15-minute Settlement Interval, Base Point Deviation Charges will be determined per Section 6.6.5.1.1.1, Base Point Deviation Charge for Over Generation, and Section 6.6.5.1.1.2, Base Point Deviation Charge for Under Generation.

(3)	The charge to each QSE for non-excused over-generation of each IRR that is not included in an IRR Group at each Resource Node Settlement Point during a 15-minute Settlement Interval, is calculated as follows:

If the flag signifying that the IRR has received a Base Point below the HDL used by SCED is not set in all SCED intervals within the 15-minute Settlement Interval:

BPDAMT q, r, p, i =	0

Otherwise, if the flag signifying that the IRR has received a Base Point below the HDL used by SCED is set in all SCED intervals within the 15-minute Settlement Interval:

BPDAMT q, r, p, i =	Max (PR1, RTSPP p, i) * OGENIRR q, r, p, i

Where:

OGENIRR q, r, p, i   = Max [0, TWTG q, r, p, i  – ¼ * AABP q, r, p, i *  (1 + KIRR)]

TWTG q, r, p, i	=       ( (AVGTG5M q, r, p, i, y) / 3) * ¼

(4)	The charge to each QSE for non-excused over-generation of each IRR that is included in an IRR Group, at each Resource Node Settlement Point, if the Real-Time metered generation is greater than the upper tolerance during a 15-minute Settlement Interval, is calculated as follows:

If the flag signifying that the IRR has received a Base Point below the HDL used by SCED is not set in all SCED intervals within the 15-minute Settlement Interval for any of the IRRs within an IRR Group, then for all IRRs within an IRR Group:

BPDAMT q, r, p =	0

If the flag signifying that the IRR has received a Base Point below the HDL used by SCED is set in all SCED intervals within the 15-minute Settlement Interval for any of the IRRs within an IRR Group, then the deviation penalty is determined for the IRR Group and evenly allocated and charged to each IRR within that IRR Group:

BPDAMT q, r, p = Max (PR1, RTSPPp) * OGENIRR q, r, i

Where:

OGENIRR q, r, i   = Max [0, TWTG q, wg, i  – ¼ * AABP q, wg, i *  (1 + KIRR)] / N

TWTG q, wg, i	=      (TWTG q, r, p, i)

AABP q,wg, i = (AABP q, r, p, i)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| BPDAMT q, r, p, i | $ | Base Point Deviation Charge per QSE per Settlement Point per Resource—The charge to QSE q for Generation Resource r at Resource Node p, for its deviation from Base Point, for the 15-minute Settlement Interval i. |
| RTSPP p, i | $/MWh | Real-Time Settlement Point Price per Settlement Point—The Real-Time Settlement Point Price at Resource Node p, for the 15-minute Settlement Interval i. |
| TWTG q, r, p, i | MWh | Time-Weighted Telemetered Generation per QSE per Settlement Point per Resource—The telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the 15-minute Settlement Interval i. |
| AABP q, r, p, i | MW | Adjusted Aggregated Base Point Generation per QSE per Settlement Point per Resource—The aggregated Base Point adjusted for Ancillary Service deployments, of Generation Resource or Controllable Load Resource r represented by QSE q at Settlement Point p, for the 15-minute Settlement Interval i. |
| AVGTG5M q, r, p, i, y | MW | Average Telemetered Generation for the 5 Minutes—The average telemetered generation of Generation Resource r represented by QSE q at Resource Node p, for the five-minute clock interval y, within the 15-minute Settlement Interval i. |
| OGENIRR q, r, p, i | MWh | Over Generation Volumes per QSE per Settlement Point per IRR Generation Resource—The amount over generated by the IRR r represented by QSE q at Resource Node p for the 15-minute Settlement Interval i. |
| PR1 | $/MWh | The price to use for the charge calculation when RTSPP is less than $20/MWh, $20/MWh. |
| KIRR | none | The percentage tolerance for over-generation of an IRR, 10%. |
| N | none | The number of IRRs within an IRR Group. |
| q | none | A QSE. |
| p | none | A Settlement Point. |
| r | none | An IRR Generation Resource not carrying an Ancillary Service Resource Responsibility or an IRR within an IRR Group where no member of the IRR Group is carrying an Ancillary Service Resource Responsibility. |
| i | none | A 15-minute Settlement Interval. |
| y | none | A five-minute clock interval in the Settlement Interval. |
| wg | none | An IRR Group. |

- 8.1.1.4.1	Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance

(1)	ERCOT shall limit the deployment of Regulation Service of each QSE for each LFC cycle equal to 125% of the total amount of Regulation Service in the ERCOT System divided by the number of control cycles in five minutes.

(2)	For those Resources that do not have a Resource Status of ONDSR or ONDSRREG or IRR Groups with no member IRR having a status of ONDSR or ONDSRREG, ERCOT shall compute the GREDP for each Generation Resource that is On-Line and released to SCED Base Point Dispatch Instructions.  The GREDP is calculated for each five-minute clock interval as a percentage and in MWs for those Resources with a Resource Status that is not ONDSR or ONDSRREG as follows:

GREDP (%) = ABS[((ATG – AEPFR)/(ABP + ARI)) – 1.0] * 100

GREDP (MW) = ABS(ATG – AEPFR – ABP - ARI)

Where:

ATG = Average Telemetered Generation = the average telemetered generation of the Generation Resource or for the aggregate of the IRRs within a IRR Group for the five-minute clock interval

ARI = Average Regulation Instruction = the amount of regulation that the Generation Resource or IRR Group should have produced based on the LFC deployment signals, calculated by LFC, during each five-minute clock interval

∆frequency is actual frequency minus 60 Hz

EPFR = Estimated Primary Frequency Response (MW) = if │∆frequency│≤ Governor Dead-Band then EPFR = zero, if not then if ∆frequency > zero, EPFR = (∆frequency - Governor Dead-Band)/((droop value * 60) – Governor Dead-Band) * HSL * -1, if not then if ∆frequency < zero, EPFR = (∆frequency + Governor Dead-Band)/((droop value * 60) – Governor Dead-Band) * HSL * -1

AEPFR = Average Estimated Primary Frequency Response = the Estimated Primary Frequency Response (MW) will be calculated every four seconds using a Resource specific droop value where 5% droop = 0.05 the Governor Dead-Band (Hz) and Resource HSL (MW) provided by the Resource Entity, and the frequency deviation (Hz) from 60 Hz and averaged for the five-minute clock interval.  For Combined Cycle Generation Resources, or Generation Resources that have been approved to telemeter Non-Frequency Responsive Capacity (NFRC), the HSL will be reduced by the telemetered NFRC MW to calculate the EPFR.  For Combined Cycle Generation Resources, 5.78% Governor droop shall be used.  The Resource-specific calculations will be aggregated for IRR Groups.

ABP = Average Base Point = the time-weighted average of a linearly ramped Base Point or sum of Base Points for IRR Groups, for the five-minute clock interval.  The linearly ramped Base Point is calculated every four seconds such that it ramps from its initial value to the SCED Base Point over a five-minute period.  The initial value of the linearly ramped Base Point will be the four-second value of the previous linearly ramped Base Point at the time the new SCED Base Point is received into the ERCOT Energy Management System (EMS).  In the event that the SCED Base Point is received after the five-minute ramp period, the linearly ramped Base Point will continue at a constant value equal to the ending four-second value of the five-minute ramp.

(3)	For all of a QSE’s Resources that have a Resource Status of ONDSR or ONDSRREG (“Dynamically Scheduled Resource (DSR) Portfolio”), ERCOT shall calculate an aggregate GREDP as a percentage and in MWs for those Resources as follows:

GREDP (%) = ABS[(∑DSR ATG – ∑DSR DBPOS + Intra-QSE Purchase – Intra-QSE Sale – ARRDDSRLR – ANSDDSRLR – ∑DSR AEPFR) / (ATDSRL + ∑DSR ARI) – 1.0] * 100

GREDP (MW) = ABS(∑DSR ATG – ∑DSR DBPOS – ATDSRL– ARRDDSRLR – ANSDDSRLR + Intra-QSE Purchase - Intra-QSE Sale – ∑DSR AEPFR – ∑DSR ARI)

Where:

∑DSR ATG = Sum of Average Telemetered Generation for all Resources with a Resource Status of ONDSR or ONDSRREG of the QSE for the five-minute clock interval

∑DSR ARI = Sum of Average Regulation Instruction for all Resources with a Resource Status of ONDSR or ONDSRREG of the QSE for the five-minute clock interval

ATDSRL = Average Telemetered DSR Load = the average telemetered DSR Load for the QSE for the five-minute clock interval

Intra-QSE Purchase = Energy Trade where the QSE is both the buyer and seller with the flag set to “Purchase”

Intra-QSE Sale = Energy Trade where the QSE is both the buyer and seller with the flag set to “Sale”

∑DSR AEPFR = Sum of Average Estimated Primary Frequency Response for all Resources with a Resource Status of ONDSR or ONDSRREG of the QSE for the five-minute clock interval

∑DSR DBPOS = Sum of the difference between a linearly ramped Base Point minus Output Schedule for all Resources with a Resource Status of ONDSR or ONDSRREG of the QSE for the five-minute clock interval.  The linearly ramped Base Point is calculated every four seconds such that it ramps from its initial value to the SCED Base point over a five minute period

ARRDDSRLR = Average Responsive Reserve Deployment DSR Load Resource = the average RRS energy deployment for the five-minute clock interval from Load Resources that are part of the DSR Load

ANSDDSRLR = Average Non-Spin Deployment DSR Load Resource = the average Non-Spin energy deployment for the five-minute clock interval from Load Resources that are part of the DSR Load

(4)	For Controllable Load Resources that have a Resource Status of ONRGL or ONCLR, ERCOT shall compute the CLREDP.  The CLREDP will be calculated both as a percentage and in MWs as follows:

CLREDP (%) = ABS[((ATPC + AEPFR)/(ABP – ARI)) – 1.0] * 100

CLREDP (MW) = ABS(ATPC – (ABP – AEPFR – ARI))

Where:

ATPC = Average Telemetered Power Consumption = the average telemetered power consumption of the Controllable Load Resource for the five-minute clock interval

ARI = Average Regulation Instruction = the amount of regulation that the Controllable Load Resource should have produced based on the LFC deployment signals, calculated by LFC, during each five-minute clock interval.  Reg-Up is considered a positive value for this calculation

AEPFR = Average Estimated Primary Frequency Response = the Estimated Primary Frequency Response (MW) will be calculated every four seconds using a Resource specific droop value where 5% droop = 0.05, the Governor Dead-Band (Hz) and Resource HSL (MW) provided by the Resource Entity, and the frequency deviation (Hz) from 60 Hz and averaged for the five-minute clock interval

ABP = Average Base Point = the time-weighted average of a linearly ramped Base Point for the five-minute clock interval.  The linearly ramped Base Point is calculated every four seconds such that it ramps from its initial value to the SCED Base Point over a five-minute period.  The initial value of the linearly ramped Base Point will be the four second value of the previous linearly ramped Base Point at the time the new SCED Base Point is received into the ERCOT EMS.  In the event that the SCED Base Point is received after the five minute ramp period, the linearly ramped Base Point will continue at a constant value equal to the ending four second value of the five-minute ramp.

(5)	ERCOT shall post to the MIS Certified Area for each QSE and for all Generation Resources or WGR Groups that are not part of a DSR Portfolio, for the DSR Portfolios, and for all Controllable Load Resources:

(a)	The percentage of the monthly five-minute clock intervals during which the Generation Resource or IRR Group was On-Line and released to SCED Base Point Dispatch Instructions;

(b)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR;

(c)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, IRR or Controllable Load Resource was providing Regulation Service;

(d)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was less than 2.5 MW;

(e)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was less than 2.5 MW;

(f)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW;

(g)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW;

(h)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was greater than 5.0 MW;

(i)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was greater than 5.0 MW;

(j)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was less than 2.5 MW;

(k)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was less than 2.5 MW;

(l)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW;

(m)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW;

(n)	The percent of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was greater than 5.0 MW; and

(o)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was greater than 5.0 MW.

(6)	ERCOT shall calculate the GREDP/CLREDP under normal operating conditions.  ERCOT shall not consider five-minute clock intervals during which any of the following events has occurred:

(a)	The five-minute intervals within the 20-minute period following an event in which ERCOT has experienced a Forced Outage causing an ERCOT frequency deviation of greater than 0.05 Hz;

(b)	Five-minute clock intervals in which ERCOT has issued Emergency Base Points to the QSE;

(c)	The five-minute clock interval following the Forced Outage of any Resource within the QSE’s DSR Portfolio that has a Resource Status of ONDSR or ONDSRREG;

(d)	The five-minute clock intervals following a documented Forced Derate or Startup Loading Failure of a Generation Resource or any member IRR of an IRR Group.  Upon request of the reliability monitor, the QSE shall provide the following documentation regarding each Forced Derate or Startup Loading Failure:

(i)	Its generation log documenting the Forced Outage, Forced Derate or Startup Loading Failure;

(ii)	QSE (COP) for the intervals prior to, and after the event; and

(iii)	Equipment failure documentation which may include, but not be limited to, Generation Availability Data System (GADS) reports, plant operator logs, work orders, or other applicable information;

(e)	The five-minute clock intervals where the telemetered Resource Status is set to ONTEST such as intervals during Ancillary Service Qualification and Testing as outlined in Section 8.1.1.1, Ancillary Service Qualification and Testing, or the five-minute clock intervals during general capacity testing requirements as outlined in Section 8.1.1.2, General Capacity Testing Requirements;

(f)	The five-minute clock intervals where the telemetered Resource Status is set to STARTUP;

(g)	The five-minute clock intervals where a Generation Resource’s ABP is below the average telemetered LSL;

(h)	Certain other periods of abnormal operations as determined by ERCOT in its sole discretion; and

(i)	For a Controllable Load Resource, the five-minute clock intervals in which the computed Base Points are equal to the snapshot of its telemetered power consumption.

(7)	All Generation Resources that are not part of a DSR Portfolio, excluding IRRs, and all DSR Portfolios shall meet the following GREDP criteria for each month.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

(a)	A Generation Resource or DSR Portfolio, excluding an IRR, must have a GREDP less than the greater of X% or Y MW for 85% of the five-minute clock intervals in the month during which GREDP was calculated.

(b)	If at the end of the month during which GREDP was calculated a DSR Portfolio has a GREDP less than X% or Y MW for 85% of the five-minute clock intervals, the reliability monitor shall, at the request of the QSE with the DSR Portfolio, recalculate GREDP excluding the five-minute clock intervals following the Forced Outage of any Resource within the QSE’s DSR Portfolio that has a Resource Status of ONDSR or ONDSRREG continuing until the start of the next Operating Hour for which the QSE is able to adjust.  If the Forced Outage of the Resource occurs within ten minutes of the start of the next Operating Hour, then the reliability monitor shall not consider any of the five-minute intervals between the time of the Forced Outage and continuing until the start of the second Operating Hour for which the QSE is able to adjust.  The requesting QSE shall provide to the reliability monitor information validating the Forced Outage including the time of the occurrence of the Forced Outage and documentation of the last submitted COP status prior to the Forced Outage of the Resource for the intervals in dispute.

(c)	Additionally, all Generation Resources that are not part of a DSR Portfolio, excluding IRRs, and all DSR Portfolios will also be measured for performance specifically during intervals in which ERCOT has declared EEA Level 1 or greater.  These Resources must meet the following GREDP criteria for the time window that includes all five-minute clock intervals during which EEA was declared.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

(d)	A Generation Resource or DSR Portfolio, excluding an IRR, must have a GREDP less than the greater of X% or Y MW.  A Generation Resource or DSR Portfolio cannot fail this criteria more than three five-minute clock intervals during which EEA was declared and GREDP was calculated.  The performance will be measured separately for each instance in which ERCOT has declared EEA.

(8)	All IRRs and IRR Groups shall meet the following GREDP criteria for each month.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

(a)	An IRR or IRR Group must have a GREDP less than Z% or the ATG must be less than the expected MW output for 95% of the five-minute clock intervals in the month when the Resource or a member IRR of an IRR Group was not carrying an Ancillary Service Resource Responsibility and received a Base Point Dispatch Instruction in which the Base Point was two MW or more below the IRR’s HSL used by SCED.  The expected MW output includes the Resource’s Base Point, Regulation Service instructions, and any expected Primary Frequency Response.

(b)	An IRR or IRR Group must have a GREDP less than the greater of X% or Y MW for 85% of the five-minute clock intervals in the month during which the Resource or a member IRR of an IRR Group was carrying an Ancillary Service Resource Responsibility.

(c)	Additionally, all IRRs and IRR Groups will also be measured for performance specifically during intervals in which ERCOT has declared EEA Level 1 or greater.  These Resources and IRR Groups must meet the following GREDP criteria for the time window that includes all five-minute clock intervals during which EEA was declared.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

(d)	An IRR or IRR Group must have a GREDP less than Z% or the ATG must be less than the expected MW output.  An IRR or IRR Group cannot fail this criteria more than three five-minute clock intervals during which EEA was declared and the Resource or a member of an IRR Group was not carrying an Ancillary Service Resource Responsibility and received a Base Point Dispatch Instruction in which the Base Point was two MW or more below the IRR’s HSL used by SCED.  The performance will be measured separately for each instance in which ERCOT has declared EEA.

(e)	An IRR or IRR Group must have a GREDP less than the greater of X% or Y MW when the Resource or a member IRR of an IRR Group was carrying an Ancillary Service Resource Responsibility.  An IRR or IRR Group cannot fail this criteria more than three five-minute clock intervals during which EEA was declared.  The performance will be measured separately for each instance in which ERCOT has declared EEA.

(9)	All Controllable Load Resources shall meet the following CLREDP criteria each month.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

(a)	A Controllable Load Resource must have a CLREDP less than the greater of X% or Y MW for 85% of the five-minute clock intervals in the month during which CLREDP was calculated.

(b)	Additionally, all Controllable Load Resources will also be measured for performance specifically during intervals in which ERCOT has declared EEA Level 1 or greater.  These Resources must meet the following CLREDP criteria for the time window that includes all five-minute clock intervals during which EEA was declared.  ERCOT will report non-compliance of the following Performance criteria to the reliability monitor:

(c)	A Controllable Load Resource must have a CLREDP less than the greater of X% or Y MW.  A Controllable Load Resource cannot fail this criteria more than three five-minute clock intervals during which EEA was declared and CLREDP was calculated.  The performance will be measured separately for each instance in which ERCOT has declared EEA.

(d)	For Controllable Load Resources which are providing RRS or Non-Spin, the following intervals will be excluded from these calculations:

(i)	Five-minute clock intervals which begin ten minutes or less after a deployment of RRS was deployed to the Resource;

(ii)	Five-minute clock intervals which begin ten minutes or less after a recall of RRS when the Resource was deployed for RRS;

(iii)	Five-minute clock intervals which begin 30 minutes or less after a deployment of Non-Spin was deployed to the Resource; and

(iv)	Five-minute clock intervals which begin 30 minutes or less after a recall of Non-Spin when the Resource was deployed for Non-Spin.

(10)	The GREDP/CLREDP performance criteria in paragraphs (7) through (9) above shall be subject to review and approval by TAC.  The GREDP/CLREDP performance criteria variables X, Y, and Z shall be posted to the MIS Public Area no later than three Business Days after TAC approval.

(11)	If at the end of the month during which GREDP was calculated, a non-DSR Resource or a QSE with DSR Resources, has a GREDP less than X% or Y MW for 85% of the five-minute clock intervals, the reliability monitor shall, at the request of the QSE, recalculate GREDP excluding the five-minute clock intervals when a Resource is deployed above the unit’s ramp rate due to ramp rate sharing between energy and Regulation Service, as described in Section 6.5.7.2, Resource Limit Calculator.  The requesting QSE shall provide to the reliability monitor information validating the ramp rate violation for the intervals in dispute.