## Slide 1
ERCOT Frequency Control Report
June 2018
ERCOT
Operations Planning
PDCWG | June 13th, 2018

## Slide 2: Frequency Control
CPS1, BAAL, & RMS1

## Slide 3: Hourly CPS1 by Day
June-18 CPS1 (%): 173.66
Notes: Outliers:
6/17/18 19:00: two periods of frequency dragging < 59.92Hz. First was due to multiple Resources shutting down at the top of the hour resulting in the loss of ~400MW in the first 10min of the hour. One of the Resources was ramping down faster than its telemetered ramp rate. Second event was due to wind ramping down quickly, with REGUP exhausted (due to previous event) and ACEI at its max. Wind ramped down ~1000MW in 20mins.
06/16/18 20:00: two periods of frequency dragging. Frequency dragged first time due to wind ramping down quickly ~500MW between 20:00 and 20:10. Regulation deployed and recovered frequency. Regulation exhausted. Wind continued to ramp down ~1500MW between 20:20 and 20:45.

## Slide 4: BAAL Exceedances & Violations
There were no BAAL exceedances

## Slide 5: 15-Minute Average CPS1%
June-18 CPS1 (%): 173.66

## Slide 6: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 176.67%

## Slide 7: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 14.59 mHz

## Slide 8: Daily RMS1 of ERCOT Frequency by Month

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 15.35 mHz
Min: 13.56 mHz
Max: 18.68 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events
UTC (t-0) |  | BA |  | BA | BA | Value "A" Information (MW) |  | Value "B" Information (MW) |  | SEFRD (FRM) |  | Exclude
Date / Time | Date/Time (t-0) | Time | B to A |  | Bias |  |  |  |  | for Bias | for R1 | for data
(MM/DD/YY HH:MM:SS) | BA Time | Zone | DelFreq | Time | DelFreq | Load Loss | Adjust | Load Loss | Adjust. | (MW/0.1Hz) | (MW/0.1Hz) | error *
2/5/2018 20:04:41 | 2/5/2018 14:04:41 | CST | -0.098 | 14:04:46 | -0.098 | 0.0 | 0.0 | 816.0 | 0.0 | -829.9 | -829.9 | N
2/14/2018 12:30:17 | 2/14/2018 06:30:17 | CST | -0.105 | 6:30:21 | -0.105 | 0.0 | 0.0 | 784.2 | 0.0 | -747.7 | -747.7 | N

## Slide 19: Op. Year 2018 BAL-003 FRM Performance
FRM Performance Results for 2018 | 
2018 | Current data year (December thru November)
-381.0 | Operating Year 2019 BA Frequency Response Obligation (FRO) for next year's FRM
-381.0 | Operating Year 2018 BA Frequency Response Obligation (FRO)
-788.77 | 2018 FRM - Median Estimated Frequency Response MW/0.1Hz for BA Compliance to R1, minimum Frequency Response
-788.8 | 2018 FRM - Average Estimated Frequency Response MW/0.1 Hz using SEFRD for R1
0.0 | 2018 FRM - Regression Estimated Frequency Response MW/0.1Hz using SEFRD for R1

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 37,389,643 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 7,056,940 MWh

## Slide 23: % Energy from Wind Generation
Notes: 18.87%

## Slide 24: ERCOT System Inertia

## Slide 25: Daily Minimum System Inertia
Notes: Minimum Inertia = 235,396 MW*s on 6/10/2018.
June
Mean: 253,983
Max: 235,396 on June 10th
Min: 268,632 on June 1st

## Slide 26: Questions?
Thank you!

## Slide 27: Op. Year 2017 BAL-003 Selected Events
Notes: Frequency Bias updated from 764 to 759 in April

## Slide 28: Op. Year 2017 BAL-003 FRM Performance
Notes: Put in some history of what these values were
Updated quarterly