## Slide 1: System Protection Working Group (SPWG) Update to ROS
August 9, 2018
Genardo T. Corpuz
SPWG Chair

## Slide 2: SPWG Meeting
Meeting held on July 19 and 20
Short Circuit Case building is complete
  Current Year 2018
  Future Years 2019-2023
GIC impacts on protective relay performance
  Electromechanical relays may be susceptible
  Impact on microprocessor relays is minimal
  Momentary affect on CT performance

## Slide 3: NERC SPCS Updates
NERC SPCS representatives from ERCOT SPWG attended the meeting on 4/24 and 4/25 in Fort Worth, TX
  Glenn Hargrave, CPS
  Armin Klusman, CNP
Development of implementation guidance documents
  PRC-019 (Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection)
  PRC-024 (Generator Frequency and Voltage Protective Relay Settings)
FERC Issued Order 847 approving PRC-027-1 on June 7, 2018
  Coordination of Protection System Performance During Faults
  Effective date of 10/1/2020

## Slide 4: Transmission Operator Protection System Misoperations 2018 Q1
ERCOT Protection System Misoperations Data – 138kV and 345kV Combined

## Slide 5: Protection System Misoperations – 2018 Q1
 |  | Value
# of Misoperations | Total | 43
 | 345 kV | 14
 | 138 kV | 28
 | < 100 kV | 1
By Category | Failure to Trip | 3
 | Slow Trip | 0
 | Unnecessary Trip during Fault | 22
 | Unnecessary Trip – Non Fault | 18
 | SPS | 0
By Relay System Type | Electromechanical | 5
 | Solid State | 1
 | Microprocessor | 30
 | Other/ N/A | 7
By Equipment Protected | Line | 18
 | Transformer | 10
 | Generator | 8
 | Shunt/Series Capacitor | 0
 | Shunt/Series Reactor | 1
 | Dynamic VAR system | 0
 | Bus | 0
 | Breaker | 6

## Slide 6: Protection System Misoperations – 2018 Q1

## Slide 7: Protection System Misoperations – 2018 Q1

## Slide 8: Protection System Misoperations 2018 Q1
Summary of Human Performance Issues
  345kV auto tripped due to shorting screw left in CT shorting block for differential.
  138kV breaker overtripped due to incorrect settings. Settings issued based on incorrect CT ratio and incorrect polarization method.
  138kV breaker overtripped due to incorrect settings. Engineer that designed the project deviated from the standard and connected external current polarizing into the 411L relay current differential input without proper settings.
  138kV line overtripped due to disabled carrier equipment. It was left out of service from prior maintenance activity.

## Slide 9: Protection System Misoperations 2018 Q1
Failure to Trip/Slow Trip Misoperations
  138kV breaker failed to trip for a fault due to incorrect wiring in the control scheme. Fault was cleared by backup relays.
  138kV breaker Z2 relays failed to trip during a high resistance fault. Fault was cleared by backup relays.

## Slide 10: TRE Misoperation Workshop July 20, 2018
Hosted by Texas Reliability Entity:
  David Penney
  Mark Henry
Exercise on Correct Operation & Misoperation Scenarios
Discussed the following:
  Current landscape of Misoperations data reporting
  Historical trends in Misoperation rates
  Opportunities for improvement of root cause analysis
  Shared ideas on how to reduce the Misoperations

## Slide 11: Questions ?