## Slide 1
West Texas Congestion Overview
Chad Thompson
Congestion Management Working Group
August 13, 2018

## Slide 2: Outline
Overview of West Texas Topology
Operator Procedure language for
  Phase Shifting Transformers
  Duplicate Constraints
  Violated Constraints
  Shift Factor Cut Off

## Slide 3: West Texas Congestion
ERCOT

## Slide 4: Phase Shifting Transformers
Activate the constraint
Study the impact of the PST
Move the PST position
Deactivate the constraint if congestion is relieved

## Slide 5: Phase Shifting Transformers
Procedure Language

## Slide 6: Duplicate Constraints
In Series
  Contingency A overloads Lines 1 and 2, which are in series with each other
Common Element
  Contingencies A and B both overload Line 1
Typically activate the most heavily overloaded, or whichever constraint shows up in RTCA first
Notes: Section 4.1 “Managing Constraints in SCED”
“Whichever is first” is important, because depending on the system conditions the same contingency does not always show up first; we have seen this in West Texas during outages inside the area as a result of the outages impacting flows (69 kV contingencies near Alpine is a good example).
In the case of West Texas, even though the constraints don’t specifically meet these criteria, the congestion is all the result of the same thing, which is loss of the ability to serve the load in the area, and that is where the labeling of the constraints as redundant has originated.

## Slide 7: Duplicate Constraints
Procedure language

## Slide 8: Violated Constraints
When a constraint is violated
  If there is a RAP, make sure it’s properly modeled
  Make sure base points are being followed
  Remove Resources from ONTEST
  Move AS
  Deploy Non-Spin
  RUC
  Utilize reactive reserves where possible
Notes: Section 4.1 “Managing Constraints in SCED”

## Slide 9: Violated Constraints
When a constraint is violated
  If, after all that, the constraint is still violated
    Consider recalling a transmission outage, if that is a contributing factor
    Develop a mitigation plan

## Slide 10: Violated Constraints
Procedure language

## Slide 11: Shift Factor Cut-Off
Shift Factors greater than the absolute value of 2 %
  Regardless of Resource Status
Excludes generators not participating in SCED
  Non-modeled generators
  DC Tie “generators”