| NPRR Number | 897 | NPRR Title | Adjustments to Black Start Service (BSS) Procurement Timeline and Testing |
| --- | --- | --- | --- |
| Date |  | September 5, 2018 |  |
| Submitter’s Information |  |  |  |
| Name |  | Clif Lange |  |
| E-mail Address |  | clif@stec.org |  |
| Company |  | South Texas Electric Coop., Inc. |  |
| Phone Number |  | 361-485-6206 |  |
| Cell Number |  | 361-894-3465 |  |
| Market Segment |  | Cooperative |  |

Comments

STEC appreciates the opportunity to submit comments to this Nodal Protocol Revision Request (NPRR) and can understand the need for some of the changes in the proposed language targeting the improved timing and transparency of limitations.

While STEC agrees that additional transparency is needed for affected Transmission Service Providers (TSPs) to realize more time for the development of their Black Start Plans, STEC is concerned that the language as proposed by ERCOT regarding the solicitation of feedback from affected TSPs is too broad and could taint the independent Black Start bid evaluation by ERCOT.  While TSP feedback is important, the feedback must be limited to only those constraints/limitations that may be unknown or unidentified by ERCOT for the cranking path to the Next Start Resource.  To ensure the feedback process remains objective and transparent, the feedback should also be provided to the prospective Black Start Resource and should only encompass information from the TSP for which ERCOT could not identify in its role as the Independent System Operator (ISO).  The prospective Black Start Resource should have the opportunity to rebut any feedback provided by the affected TSP.

For the testing portions, STEC submits that the changes offered by ERCOT are new requirements and are not merely an alignment with existing practice, particularly for the Load-Carrying Test.  ERCOT has always allowed the Load-Carrying Test to be conducted by allowing the Resource to carry its own auxiliaries, which is an option that ERCOT is disallowing in its proposed language.  STEC’s experience is that carrying a smaller Load, such as station auxiliaries, is much more difficult to do than is carrying Load from a Load bank or ERCOT Customer Load.  These new requirements will likely increase the cost to conduct the testing which results in increased payments by ERCOT consumers for the service, or will lead to the interruption of ERCOT Customer Load, sometimes multiple times a day, to conduct the testing.  STEC proposes changes to the NPRR that would adopt the inclusion of pre-determined Loads from the BSS bid to be included during testing.  This allows improved planning for testing, including associated costs, and is part of current practice.

Lastly, the NPRR includes changes to paragraph (3)(c)(iv) in Section 8.1.1.2.1.5, System Black Start Capability Qualification and Testing.  Although the language is not new, this section includes the term “sufficient” in the context that ERCOT or the TSP shall direct the testing Resource to serve “sufficient” Load to demonstrate the Resource’s capability.   ”Sufficient” is an ambiguous term and can introduce uncertainty for the bidder.  What is “sufficient” to the bidder and becomes the basis for the bid may be something entirely different than what ERCOT or the TSP may deem to be “sufficient”.  This leads to inaccurate bids which results in increased costs to ERCOT consumers, or a financial loss to the Resource, potentially threatening the possibility of future offers from the Resource in a market that has historically realized low participation.  STEC strikes this term in its edits to this section.

Revised Cover Page Language

None

Revised Proposed Protocol Language

3.14.2	Black Start

(1)	Each Generation Resource providing BSS must meet the requirements specified in North American Electric Reliability Corporation (NERC) Reliability Standards and the Operating Guides.

(2)	Each Generation Resource providing BSS must meet technical requirements specified in Section 8.1.1, QSE Ancillary Service Performance Standards, and Section 8.1.1.1, Ancillary Service Qualification and Testing.

(3)	Bids for BSS are due on or before February 15th of each two year period.  Bids must be evaluated based on evaluation criteria attached as an appendix to the request for bids and contracted by December 31st for the following two year period.  ERCOT shall ensure BSSs are arranged, provided, and deployed as necessary to reenergize the ERCOT System following a Blackout or Partial Blackout.

(a)	Resources shall disclose any weather related limitations that could affect the Resource’s ability to provide BSS using the form provided in Section 22, Attachment M, Generation Resource Disclosure Regarding Bids for Black Start Service, as part of a bid to provide BSS.

(b)	When a Resource is selected to provide BSS, the Black Start Resource shall be required to complete all applicable testing requirements as specified in Section 8.1.1.2.1.5, System Black Start Capability Qualification and Testing.

(c)	ERCOT shall provide a list of all prospective Black Start Resources that responded to the RFP for BSS to the impacted TSPs no later than seven days after the date on which bids for BSS are due.  Any feedback from affected TSPs shall be limited to the identification of transmission constraints that may adversely impact the ability of the Black Start Resource to energize the Next Start Resource and shall be due to ERCOT and the QSE representing the prospective Black Start Resource by March 1st of that year.  Feedback shall not disqualify any bid, shall not delay the BSS procurement process, and shall require validation by ERCOT.  The QSE representing the Black Start Resource shall have the option to provide a response to any feedback provided by an affected TSP.

(4)	ERCOT may schedule unannounced Black Start testing, to verify that BSS is operable as specified in Section 8.1.1.2.1.5.

(5)	QSEs representing Generation Resources contracting for BSSs shall participate in training and restoration drills coordinated by ERCOT.

(6)	ERCOT shall periodically conduct system restoration seminars for all TSPs, Distribution Service Providers (DSPs), QSEs, Resource Entities and other Market Participants.

(7)	ERCOT shall periodically determine and review the location and number of Black Start Resources required, as well as any special transmission or voice communication needs required.  ERCOT and providers of this service shall meet the requirements as specified in the Operating Guides and in NERC Reliability Standards.

(8)	A Resource Entity representing a Black Start Resource may request that an alternate Generation Resource which is connected to the same black start primary and secondary cranking path as the original Black Start Resource be substituted in place of the original Black Start Resource during the two year term of an executed Standard Form Black Start Agreement (Section 22, Attachment D, Standard Form Black Start Agreement) if the alternate Generation Resource meets testing and verification under established qualification criteria to ensure BSS.

(a) 	ERCOT, in its sole discretion, may reject a Resource Entity’s request for an alternate Generation Resource and will provide the Resource Entity an explanation of such rejection.

(b) 	If ERCOT accepts the alternative Generation Resource as the substituted Black Start Resource, such acceptance shall not affect the original terms, conditions and obligations of the Resource Entity under the Standard Form Black Start Agreement.  The Resource Entity shall submit to ERCOT an Amendment to Standard Form Black Start Agreement (Section 22, Attachment I, Amendment to Standard Form Black Start Agreement) after qualification criteria has been met.

(9)	For the purpose of the Black Start Hourly Standby Fee as described in Section 6.6.8.1, Black Start Hourly Standby Fee, the Black Start Service Availability Reduction Factor shall be determined by using the availability for the original Black Start Resource and any substituted Black Start Resource(s), as appropriate for the rolling 4380 hour period of the evaluation.

(10)	Each Generation Resource selected to provide BSS shall be prepared and able to provide BSS at any time as may be required by ERCOT, subject only to the limitations described in ERCOT Protocols or the Black Start Agreement.

8.1.1.2.1.5	System Black Start Capability Qualification and Testing

(1)	A Resource is qualified to be a Black Start Resource if it has met the following requirements:

(a)	Verified control communication path performance;

(b)	Verified primary and alternate voice circuits for receipt of instructions;

(c)	Passed the “Basic Starting Test” as defined below;

(d)	Passed the “Line-Energizing Test” as defined below;

(e)	Passed the “Load-Carrying Test” as defined below;

(f)	Passed the “Next Start Resource Test” as defined below;

(g)	If not starting itself, has an ERCOT-approved firm standby power contract with deliverability under Blackout circumstances from a non-ERCOT Control Area that can be finalized upon selection as a Black Start Resource;

(h)	If not starting itself, has an ERCOT approved agreement with the necessary TSPs for access to another power pool, for coordination of switching during a Blackout or Partial Blackout, for coordination of maintenance through the ERCOT Outage Scheduler for all non-redundant transmission startup feeds;

(i)	If dependent upon non-ERCOT transmission resources, agreements providing this Transmission Service have been provided in the proposal; and

(j)	Demonstrated to ERCOT’s satisfaction that the Resource has successfully completed remediation to any weather-related limitation disclosed as part of the Black Start Service (BSS) bid.

(2)	On successful demonstration of system BSS capability, ERCOT shall certify that the Black Start Resource is capable of providing system BSS capacity and shall provide a copy of the certificate to the Resource Entity of the Black Start Resource.  Qualification shall be valid for the time frames set forth below.  Except under extenuating circumstances, as reasonably determined by ERCOT, all qualification testing for the next year of BSS must be completed by June 1st of each year.

(3)	ERCOT may limit the number of qualification retests allowed.  Qualification retesting is required only for the aspect of system BSS capability for which the Black Start Resource failed.  If a Black Start Resource under an existing Black Start Agreement does not successfully re-qualify within two months of failing a test described herein, ERCOT shall decertify the Black Start Resource for the remainder of the calendar year as described in Section 7, Black Start Decertification, of Section 22, Attachment D, Standard Form Black Start Agreement.  The following tests are required for BSS qualification:

(a)	The “Basic Starting Test” includes the following:

(i)	The basic ability of the Black Start Resource to start itself, or start from a normally open interconnection to another provider not inside the ERCOT interconnection, without support from the ERCOT System;

(ii)	Annual testing, either as a stand-alone test or part of the Line Energizing and Load-Carrying Tests, and the test is performed during a one-week period agreed to in advance by the Black Start Resource and ERCOT and must not cause outage to ERCOT Customer Load or the availability of other Resources to the ERCOT market;

(iii)	Confirmation of the dates of the test with the Black Start Resource by ERCOT;

(iv)	Isolation of the Black Start Resource, including all auxiliary Loads, from the ERCOT System, except for the transmission that connects the Resource to a provider not inside the ERCOT interconnection if the startup power is supplied by a firm standby contract.  Black Start Resources starting with the assistance of a provider not inside the ERCOT interconnection through a firm standby agreement will connect to provider not inside the ERCOT interconnection, start-up, carry internal Load, disconnect from the provider not inside the ERCOT interconnection if not supplied through a black-start capable DC Tie, and continue equivalently to what is required of other Black Start Resources;

(v)	The ability of the Black Start Resource to start without assistance from the ERCOT System, except for the transmission that connects the Resource to a provider not inside the ERCOT interconnection if the startup power is supplied by a firm standby contract;

(vi)	The ability of the Black Start Resource to remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or Loads in the immediate area for at least 30 minutes;

(vii)	The Black Start Resource must have verified that its Volts/Hz relay, over-excitation limiter, and under-excitation limiter are set properly and that no protection devices will trip the Black Start Resource within the required reactive range.  The Resource Entity for the Black Start Resource shall provide ERCOT with data to verify these settings; and

(viii)	Each Black Start Resource must pass a Basic Starting Test once each calendar year.

(b)	The “Line-Energizing Test” must be conducted at a time agreed on by the Black Start Resource, TSP or Distribution Service Provider (DSP), and ERCOT and includes the following:

(i)	Energizing transmission with the Black Start Resource when conditions permit as determined by the TSP or DSP but at least once every three years;

(ii)	De-energizing sufficient transmission in such manner that when energized by the Black Start Resource it demonstrates the Black Start Resource’s ability to energize enough transmission to deliver to the Loads the Resource’s output that ERCOT’s restoration plan requires the Black Start Resource to supply.  ERCOT shall be responsible for transmission connections and operations that are compatible with the capabilities of the Black Start Resource;

(iii)	Conducting a Basic Starting Test;

(iv)	Energizing transmission with the Black Start Resource of the previously de-energized transmission, while monitoring frequency and voltages at both ends of the line.  Alternatively, if ERCOT agrees, the transmission line may be connected to the Black Start Resource before starting, allowing the Resource to energize the line as it comes up to speed;

(v)	Stable operation of the Black Start Resource (in both frequency and voltage) while supplying only its auxiliary Loads or external Loads for at least 30 minutes;

(vi)	This test may be performed together with the Basic Starting Test in one 30 minute interval; and

(vii)	Each Black Start Resource must pass a Line-Energizing Test once every three years.

(c)	The “Load-Carrying Test” shall utilize the Load identified in the BSS bid, unless otherwise agreed to between ERCOT and the BSS bidder.  The Load may be the Resource’s own auxiliary Load, ERCOT Customer Load subject to the provisions within this paragraph, or alternative loads, such as load banks.  ERCOT shall not require the BSS bidder to utilize a Load other than what was proposed by the BSS bidder unless there is strong reason to believe that the Black Start Resource will not be stable in both voltage and frequency with the proposed Load.  ERCOT Customer Load shall not be interrupted for purposes of this test unless it was proposed as part of the BSS bid submission, or ERCOT has reason to believe that the Load proposed by the BSS bidder will not provide stable operation of the Black Start Resource.  Should interruption of ERCOT Customer Load be deemed necessary for purposes of this test, ERCOT shall coordinate with the TSP or DSP that serves the affected Load to ensure that the affected ERCOT Customer Load is notified of the testing.  Testing shall occur as conditions permit, at a time agreed on by the Black Start Resource, TSP or DSP, and ERCOT, and includes the following:

(i)	Stable operation of the Black Start Resource (in both frequency and voltage) while supplying restoration power to Load  ;

(ii)	Conducting a Basic Starting Test;

(iii)	Conducting a Line-Energizing Test when required;

(iv)	Under the direction of ERCOT or the TSP operator, the Black Start Resource shall demonstrate the Black Start Resource’s capability to supply the required Load identified in paragraph (c) above, while maintaining voltage and frequency for at least 30 minutes;

(v)	This test may be performed together with the Basic Starting Test and Line Energizing Test when required in one 30 minute interval; and

(vi)	Qualification under the Load-Carrying Test is valid for five years.

(d)	“Next Start Resource Test”:

(i)	The ability of a Black Start Resource to start up the next start unit’s largest required motor while continuing to remain stable and control voltage and frequency shall be tested.  This test shall be repeated when a new next start unit is selected;

(ii)	To pass the test:

(A)	The potential Black Start Resource must start the next start unit (as determined by ERCOT), or start the next start unit’s largest required motor and satisfied the next start unit’s minimum startup Load requirements; or

(B)	The Resource Entity shall demonstrate to the satisfaction of ERCOT through simulation studies conducted by the Resource Entity or a qualified third party, that the potential Black Start Resource is capable of starting the next start unit’s largest required motor while meeting the next start unit’s minimum startup Load requirements.

(iii)	Potential BSS bidders may request next start unit information from ERCOT prior to the selection process to satisfy this requirement.  ERCOT shall request this information from the designated next start unit as follows:  ERCOT may require any Generation Resource to provide largest motor startup information and unit startup energy requirements as needed to validate Black Start proposals or plans submitted by other Generation Resources.  Such data, if requested by ERCOT, shall be provided by the QSE representing the Generation Resource or the Generation Resource Entity to ERCOT within 30 days.  Such information shall be considered Protected Information by the requesting Resource Entity when provided to the Resource Entity;

(iv)	If a physical test is performed, the test shall commence with a Basic Starting Test, followed by a Line Energizing Test when required and a Load-Carrying Test as a stand-alone test or part of the Next Start Resource Test;

(v)	If a physical test is performed, the Black Start Resource must remain stable (in both voltage and frequency) and controlling voltage for 30 minutes;

(vi)	If a physical test is performed, this test may be performed together with the Basic Starting Test, Line Energizing Test when required, and Load-Carrying Test in one 30 minute interval; and

(vii)	Each Black Start Resource must pass the Next Start Resource Test once every five years.

(4)	Each qualified Black Start Resource shall perform a Black Start Resource Availability Test quarterly unless the Black Start Resource has successfully started and operated at LSL or higher for at least four consecutive Settlement Intervals during the quarter.  The Black Start Resource’s cost to perform a Black Start Availability Test may be a component of the overall bid for BSS but ERCOT will not separately compensate QSEs representing Black Start Resources for such testing.  ERCOT, at its sole discretion, may grant an exemption of the Black Start Resource Availability Test for QSEs whose Black Start Resources have responded as instructed by ERCOT during an EEA event.

(5)	The Black Start Resource Availability Test shall be scheduled by ERCOT.  Upon receipt of notification for a Black Start Resource Availability Test, the QSE representing the Black Start Resource shall send confirmation to ERCOT of its intent to comply with the test or submit a request to reschedule along with justification for the request.

(6)	ERCOT shall provide the QSE representing the Black Start Resource two-hour notice in order to allow the QSE time to update its COP.  The QSE representing the Black Start Resource shall show the Resource as “ONTEST” in its COP and through its Real-Time telemetry for the duration of the test.  As part of the Black Start Resource Availability Test, the QSE representing the Black Start Resource shall start the Black Start Resource and operate it at or above its LSL for at least four consecutive Settlement Intervals.  After completion of the Black Start Resource Availability Test the QSE will update its COP to reflect their current status.

(7)	Upon completion of the Black Start Resource Availability Test, the QSE representing the Black Start Resource shall complete and file a Black Start Resource Availability Test report with ERCOT.  If the Black Start Resource wants to use a successful start and normal operation to satisfy the quarterly reporting requirement, it must provide the necessary information for the start and normal operation on a Black Start Resource Availability Test report.  The report form shall be provided by ERCOT.

(8)	A Black Start Resource Availability Test is deemed to be successful if the Black Start Resource comes On-Line within the time specified in the Black Start Resource’s RFP response submitted to ERCOT and operates at a minimum level as agreed to by ERCOT and the QSE representing the Black Start Resource for at least four consecutive Settlement Intervals.

(9)	If the Black Start Resource fails to successfully start during the Black Start Resource Availability Test, the QSE representing the Black Start Resource shall immediately update its Availability Plan for that Black Start Resource showing zero availability.  The QSE representing the Black Start Resource shall not receive the Hourly Standby Fee for BSS effective from the date of the failed Black Start Resource Availability Test.  The QSE representing the Black Start Resource may schedule a second Black Start Resource Availability Test, subject to ERCOT approval, to be completed within ten Business Days of the date of the failed Black Start Resource Availability Test unless a later date is agreed to by ERCOT.  The cost of the second Black Start Resource test will be borne solely by the QSE representing the Black Start Resource.

(10)	If the Black Start Resource successfully passes the second Black Start Resource Availability Test, the QSE representing the Black Start Resource shall resume receipt of the Hourly Standby Fee beginning on the date of the successful Black Start Resource Availability Test.

(11)	If the Black Start Resource fails a second Black Start Resource Availability Test within the quarter, it shall immediately be disqualified from providing BSS and shall receive no further compensation under the Black Start Service Agreement.  In addition, ERCOT shall claw-back all Hourly Standby Fee payments made to the QSE representing the Black Start Resource since its last successful Black Start Resource Availability Test or its last successful start and operation under normal system conditions, whichever is later.  The clawed-back Hourly Standby Fee payments shall be uplifted by ERCOT to Loads on a Load Ratio Share (LRS) basis.  ERCOT may, at its sole discretion, consider allowing the Black Start Resource to perform an additional Black Start Resource Availability Test.  ERCOT may also, at its sole discretion, seek to procure additional Black Start Resources to replace the disqualified Black Start Resource.

(12)	A QSE representing the Black Start Resource shall update its Availability Plan for a Black Start Resource to show zero if the Black Start Resource fails to perform when ERCOT has issued a Dispatch Instruction to come On-Line any time other than for a Blackout.  The Black Start Resource shall continue to be shown as unavailable until it successfully starts under normal operations or completes a successful Black Start Resource Availability Test.

(13)	If the Black Start Resource fails to perform successfully during an actual Blackout and the Black Start Resource has been declared available, as defined in Section 22, Attachment D, ERCOT shall:

(a)	Decertify the Black Start Resource for the remainder of the Black Start Agreement contract term, and

(b)	Claw-back 100% of the Hourly Standby Fee paid to the QSE representing the Black Start Resource for all the Operating Days since its last successful Black Start Resource Availability Test or its last successful start and operation under normal system conditions, whichever is later.

ERCOT Nodal Protocols

Section 22

Attachment M:  Generation Resource Disclosure Regarding Bids for Black Start Service

- TBD, 20XX

Generation Resource Disclosure regarding Bids for Black Start Service

Resource Entity:

Qualified Scheduling Entity (QSE) representing the Resource Entity:

Generation Resource (list by Resource Site Code):

Operational Weather limitations:

(1)	Minimum Ambient Operation Temperature (°F) 	________________________

(2)	Maximum Ambient Operation Temperature (°F)	________________________

(3)	Relative Humidity (%)________________________________________________

Weather Related Limitation Disclosure:

Please list any weather-related limitations to the Generation Resource’s start-up/operation capabilities (include a brief description of the limitation(s), planned remediation for the   limitation, and an associated target completion date for the remediation): __________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Weatherization affirmation – please affirm by checking the box:

[_] I hereby affirm that all disclosed weather related limitations listed above and weatherization preparations for equipment critical to providing Black Start service are complete or will be completed prior to the beginning of Black Start Qualification Testing.

By signing below, I certify that I am an officer or authorized executive of each Resource Entity listed above, that I am authorized to execute and submit this declaration on behalf of each Resource Entity listed above, and that the statements contained herein are true and correct.

______________________________________

Signature

______________________________________

Name

______________________________________

Title

______________________________________

Date