## Slide 1
ERCOT Frequency Control Report
July 2018
ERCOT
Operations Planning
PDCWG | August 23rd, 2018

## Slide 2: Frequency Control
CPS1, BAAL, & RMS1

## Slide 3: Hourly CPS1 by Day
July-18 CPS1 (%): 176.45
Notes: Outliers:
7/1/18 11:00: 98.64%
Wind ramped down roughly 1500MW through the hour. Multiple resources with expected generation <-30MW between 11:40 and 11:55.
7/3/18 0:00: 83.67%
Wind ramped down roughly 3754MW through the hour. Regulation exhausted from 12:10 AM through the end of the hour. Frequency never got low enough to warrant a manual offset by the ERCOT operator. Frequency sat between 59.98 and 59.95 for almost entire hour.

## Slide 4: 7/3/18 0:00 CPS1 Outlier
Frequency
Wind

## Slide 5: 7/3/18 0:00 CPS1 Outlier
Chart: 5-min GTBD Error Due to Wind Ramp| 7/2/18 22:00 to 7/3/18 3:00
| 22:00 | 22:05 | 22:10 | 22:15 | 22:20 | 22:25 | 22:30 | 22:35 | 22:40 | 22:45 | 22:50 | 22:55 | 23:00 | 23:05 | 23:10 | 23:15 | 23:20 | 23:25 | 23:30 | 23:35 | 23:40 | 23:45 | 23:50 | 23:55 | 0:00 | 0:05 | 0:10 | 0:15 | 0:20 | 0:25 | 0:30 | 0:35 | 0:40 | 0:45 | 0:50 | 0:55 | 1:00 | 1:05 | 1:10 | 1:15 | 1:20 | 1:25 | 1:30 | 1:35 | 1:40 | 1:45 | 1:50 | 1:55 | 2:00 | 2:05 | 2:10 | 2:15 | 2:20 | 2:25 | 2:30 | 2:35 | 2:40 | 2:45 | 2:50 | 2:55
Error | -69.4922 | -369.9639 | -178.3428 | -84.8721 | -95.2598 | -156.3213 | -372.7979 | -363.0518 | -158.4346 | -185.3281 | -279.3535 | -144.7559 | -64.2393 | -35.6182 | 41.1787 | 78.8525 | -34.7021 | -47.1807 | 51.7217 | 3.1016 | 68.0508 | 29.4355 | 135.7627 | 175.4629 | 233.5186 | 204.377 | 254.8594 | 283.6748 | 264.1992 | 340.1504 | 326.8838 | 345.665 | 446.9189 | 366.5605 | 341.5645 | 343.3638 | 253.4204 | 303.54 | 345.3755 | 299.5464 | 293.8818 | 264.897 | 174.396 | 177.9204 | 195.0234 | 155.2549 | 88.6191 | 106.603 | 144.6162 | 84.4404 | 164.147 | 131.084 | 79.0771 | 23.7222 | 7.4961 | 79.8716 | 107.3506 | 14.8555 | 6.2046 | -1.8999
Error (w/ PWRR) | -3.3926 | -340.7646 | -126.8428 | 13.0273 | 17.3389 | -67.0234 | -287.7969 | -294.1514 | -26.834 | -31.5283 | -130.5537 | -8.2559 | 63.6592 | 96.3809 | 150.8789 | 163.8535 | 2.998 | -44.2803 | 49.8223 | 10.7031 | 41.3506 | 11.0361 | 107.5615 | 157.6621 | 195.2188 | 131.7773 | 168.0605 | 182.374 | 130.001 | 197.6494 | 156.9834 | 179.3672 | 255.918 | 167.1611 | 119.8652 | 101.4644 | 15.4204 | 93.9399 | 129.8755 | 122.8462 | 95.3823 | 86.6973 | -17.7036 | -1.9795 | 45.8232 | 24.6548 | -45.2803 | -2.4971 | 62.2158 | 6.2407 | 90.0464 | 62.6841 | 12.6772 | -54.478 | -64.8037 | 35.9717 | 83.7505 | -2.2441 | -30.6958 | -24.4995
Forecasted ramp calculated using intra-hour wind forecast (IHWF) that will be put into GTBD via SCR 795 (PWRR)
GTBD error due to wind ramping is due to persistence logic, where wind is assumed to be doing in 5-min what it is doing currently (constant). During wind ramps, regulation used to make up lost or gained MW. PWRR via SCR795 reduces GTBD error in this specific CPS1 outlier.

## Slide 6: BAAL Exceedances & Violations
There were no BAAL exceedances

## Slide 7: 15-Minute Average CPS1%
July-18 CPS1 (%): 176.45

## Slide 8: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 176.41%

## Slide 9: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 14.57 mHz

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Daily RMS1 of ERCOT Frequency by Month

## Slide 12: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 14.51 mHz
Min: 12.34 mHz
Max: 17.28 mHz

## Slide 13: Frequency Profile Comparison

## Slide 14: Frequency Profile Comparison

## Slide 15: Frequency Profile Comparison

## Slide 16: Time Error Correction

## Slide 17: ERCOT Daily Time Error

## Slide 18: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 19: BAL-003 Performance

## Slide 20: Op. Year 2018 BAL-003 Selected Events
 | BA |  | BA | BA | Value "A" Information (MW) |  | Value "B" Information (MW) |  | SEFRD (FRM) |  | Exclude
Date/Time (t-0) | Time | B to A |  | Bias |  |  |  |  | for Bias | for R1 | for data
BA Time | Zone | DelFreq | Time | DelFreq | Load Loss | Adjust | Load Loss | Adjust. | (MW/0.1Hz) | (MW/0.1Hz) | error *
2/5/2018 14:04:41 | CST | -0.098 | 14:04:46 | -0.098 | 0.0 | 0.0 | 816.0 | 0.0 | -829.9 | -829.9 | N
2/14/2018 06:30:17 | CST | -0.105 | 6:30:21 | -0.105 | 0.0 | 0.0 | 784.2 | 0.0 | -747.7 | -747.7 | N
3/5/2018 00:51:20 | CST | -0.033 | 6:51:20 | -0.033 | 0.0 | 0.0 | 513.5 | 0.0 | -1552.2 | -1552.2 | N
3/24/2018 15:47:15 | CDT | -0.085 | 20:47:15 | -0.085 | 0.0 | 0.0 | 797.3 | 0.0 | -943.3 | -943.3 | N
3/29/2018 10:09:40 | CDT | -0.041 | 16:09:40 | -0.041 | 0.0 | 0.0 | 434.1 | 0.0 | -1049.1 | -1049.1 | N
4/13/2018 20:02:08 | CDT | -0.076 | 2:02:08 | -0.076 | 0.0 | 0.0 | 438.0 | 0.0 | -577.9 | -577.9 | N
4/14/2018 19:11:25 | CDT | -0.048 | 1:11:25 | -0.048 | 0.0 | 0.0 | 349.0 | 0.0 |  |  | Y
4/28/2018 12:15:43 | CDT | -0.048 | 18:15:43 | -0.048 | 0.0 | 0.0 | 408.0 | 0.0 |  |  | Y
5/5/2018 10:19:04 | CDT | -0.095 | 16:19:04 | -0.095 | 0.0 | 0.0 | 536.3 | 0.0 | -563.5 | -563.5 | N
5/21/2018 02:06:23 | CDT | -0.081 | 8:06:23 | -0.081 | 0.0 | 0.0 | 460.5 | 0.0 | -568.4 | -568.4 | N
Maybe. Will be valuated at the end of the year.

## Slide 21: Op. Year 2018 BAL-003 FRM Performance
FRM Performance Results for 2018 | 
2018 | Current data year (December thru November)
-381.0 | Operating Year 2019 BA Frequency Response Obligation (FRO) for next year's FRM
-381.0 | Operating Year 2018 BA Frequency Response Obligation (FRO)
-788.77 | 2018 FRM - Median Estimated Frequency Response MW/0.1Hz for BA Compliance to R1, minimum Frequency Response
-854.0 | 2018 FRM - Average Estimated Frequency Response MW/0.1 Hz using SEFRD for R1
0.0 | 2018 FRM - Regression Estimated Frequency Response MW/0.1Hz using SEFRD for R1

## Slide 22: ERCOT Energy Statistics

## Slide 23: Total Energy
Notes: 39,656,104 MWh

## Slide 24: Total Energy from Wind Generation
Notes: 4,293,939 MWh

## Slide 25: % Energy from Wind Generation
Notes: 10.83%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 245,095 MW*s on 7/1/2018.
July
Mean: 302,996
Max: 355,780 on July 20th
Min: 245,095 on July 1st

## Slide 28: Questions?
Thank you!

## Slide 29: Op. Year 2017 BAL-003 Selected Events
Notes: Frequency Bias updated from 764 to 759 in April

## Slide 30: Op. Year 2017 BAL-003 FRM Performance