| NOGRR Number | 180 | NOGRR Title | Exemption of Governor Dead-Band and Droop Setting Requirements for Steam Turbines of Combined Cycle Generation Resources |
| --- | --- | --- | --- |
| Date of Decision |  | August 9, 2018 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined |  |
| Priority and Rank Assigned |  | To be determined |  |
| Nodal Operating Guide Sections Requiring Revision |  | 2.2.7, Turbine Speed Governors |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) removes Governor Dead-Band and Governor droop settings requirements for steam turbines of Combined Cycle Generation Resources. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | Most Combined Cycle Generation Resources in the ERCOT Region operate with combustion turbines capable of responding to frequency deviations using Governor controls, but the associated steam turbines are not capable of providing a response. Per paragraph (3) of Section 2.2.7, combustion turbines of Combined Cycle Resources have a droop setting requirement of 4%. Combined Cycle Generation Resources’ Primary Frequency Response performance is evaluated at 5.78% droop to account for the steam turbine of the combined cycle train that does not characteristically respond to frequency like other Generation Resources. Eliminating Governor setting requirements for steam turbines of Combined Cycle Generation Resources will align the Nodal Operating Guide with current operational practice. |  |
| ROS Decision |  | On 7/12/18, ROS voted unanimously to table NOGRR180 and refer the issue to the Performance, Disturbance, Compliance Working Group (PDCWG). All Market Segments were present for the vote. On 8/9/18, ROS voted unanimously to recommend approval of NOGRR0180 as submitted. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 7/12/18, there was no discussion. On 8/9/18, there was no discussion. |  |

| Sponsor |  |
| --- | --- |
| Name | Colleen Frosch |
| E-mail Address | Colleen.frosch@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4219 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed Guide Language Revision

2.2.7	Turbine Speed Governors

(1)	A Governor shall be in-service whenever the All-Inclusive Generation Resource is connected to the ERCOT Transmission Grid.

(2)	Generation Resources that have not been evaluated in at least eight Frequency Measurable Events (FMEs) within 36 months shall conduct Governor performance tests for that Generation Resource within 12 months using one of the test methods or historical methods specified in Section 8, Attachment C, Turbine Governor Speed Tests.  The Resource Entity shall then provide test results to ERCOT.

(3)	All-Inclusive Generation Resources, except steam turbines of Combined Cycle Generation Resources, shall have a Governor droop characteristic and Governor Dead-Band setting no greater than those shown below in Table 1, Maximum Governor Dead-Band Settings, and Table 2, Maximum Governor Droop Settings, as defined below:

Table 1: Maximum Governor Dead-Band Settings

| Generator Type | Max. Deadband |
| --- | --- |
| Steam Turbines with Mechanical Governors | +/- 0.034 Hz |
| Hydro Turbines with Mechanical Governors | +/- 0.034 Hz |
| All Other Generating Units/Generating Facilities | +/- 0.017 Hz |
| Controllable Load Resources (CLRs) | +/- 0.036 Hz |

Table 2: Maximum Governor Droop Settings

| Generator Type | Max. Droop % Setting |
| --- | --- |
| Combustion Turbine (Combined Cycle) | 4% |
| All Other Generating Units/Generating Facilities/ CLRs | 5% |

(4)	If ERCOT determines that ERCOT System reliability would be enhanced, for a defined period of time, ERCOT may direct Wind-powered Generation Resources (WGRs) under the control of a Remedial Action Scheme (RAS) to limit power increases due to frequency if there is risk of an RAS operation due to a low frequency FME.