## Slide 1: LCRA Freeze protection
Presented by: Jason Kessel
Created by: Jack Sandel

## Slide 2: Agenda
Background
Heat Tracing Issues
Transmitters
Thermocouples
Scaffold Wrap

## Slide 3: Background
Sim Gideon
3 Conventional Gas Fired Drum Units
Capacity ~ 607 MW
Lost Pines
2x1 Combined Cycle
Natural Gas
Capacity ~ 510 MW
Winchester
4 Simple Cycle
Natural Gas
Capacity ~ 176 MW

## Slide 4: Background

## Slide 5: Heat Tracing Issues in the Past
Moisture can corrode heat trace
Insulation can fall off
Inadvertent line damage
Expensive to install and operate
Test today, fails tomorrow without notice

## Slide 6: Transmitters

## Slide 7: Transmitters
Capillary line
  Silicon fill fluid
  Freezes ~ - 40F
Reduces heat trace and insulation requirements
Works well during operation
Used for level and pressure transmitters

## Slide 8: New Transmitter Issues
Fluctuations during startup/shutdown
Readings (fluid density) affected by:
  Skin leaks
  Ambient temperature
Expensive
Still have to heat trace leg to transmitter

## Slide 9: Thermocouples
Used for critical instrumentation
Validates heat trace effectiveness
Low skill set to monitor

## Slide 10: Thermocouples
Still take amp readings
Place a thermocouple near end of heat trace
Read with Fluke meter
Thermocouple Pigtails

## Slide 11: Scaffold Wrap

## Slide 12: Scaffold Wrap
Acts as shield from wind
Shrink with open flame
Secure with rope
Reduces convective HX
Non-Flammable
More durable than tarps

## Slide 13: Scaffold Wrap
Easy to install and repair
Long lasting and effective
More cost effective than replacing tarps
Fire retardant
Lightweight

## Slide 14: Conclusion
LCRA Freeze Protection
  Gel filled transmitters
  Thermocouples
  Scaffold wrap

## Slide 15
Questions?