## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Chad Mulholland, NRG
ROS
September 6th, 2018

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    2 FMEs in the month of July
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 08/23/18
  SCT DC Tie Directive 9 – MSSC Whitepaper and Ancillary Service Requirements. Further presentation by ERCOT(overshoot on export) and discussions in September and November PDCWG Meetings.
  BAL-001-TRE-1 Performance Evaluation to check for pass/fail before scoring progress and No Evaluation of Resources below LSL especially for resources carrying RRS Responsibility Update
  Regulation & Frequency Control Reports
  Texas RE is working with ERCOT on the BAL-001-TRE-1 SAR relating to governor droop setting requirements for combined cycle units – particularly on steam units in a combined cycle.
  July 30 Frequency Disturbance not evaluated as an FME due to abnormal nadir(20 seconds as opposed to 6-10 seconds)

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 2 FMEs in July(Disturbances on 7/30
  7/6/2018 13:10:58
    Loss of 813 MW
    Interconnection Frequency Response:
    10 of 46 Evaluated Generation Resources(2 of 33 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    8 of 46 Evaluated Generation Resources(0 of 33 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.
  7/18/2018 17:44:59
    Loss of 494 MW
    Interconnection Frequency Response:
    11 of 49 Evaluated Generation Resources(6 of 31 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    12 of 49 Evaluated Generation Resources(6 of 31 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 815.90 MW/0.1Hz

## Slide 7: Frequency Control Report
July 2018

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections

## Slide 12: ERCOT Total Energy

## Slide 13: ERCOT Total Energy from Wind Generation

## Slide 14: ERCOT % Energy from Wind Generation

## Slide 15
Questions?