## Slide 1
Ancillary Service Methodology Preliminary Quantities For 2019
ERCOT Staff
Sep 15, 2018

## Slide 2: Schedule for Stakeholder Discussion
September 12, 2018 – PDCWG (2019 AS Methodology)
September 20, 2018 – OWG
Sep 24, 2018 – QMWG
October 10, 2018 – WMS
October 11, 2018 – ROS
October 25, 2018 – TAC
Dec 11, 2018 – BOD

## Slide 3: Scope of Discussion
ERCOT is not proposing any changes to the Ancillary Service (A/S) Methodology for 2019.
The A/S quantities for 2019 contained in this presentation are based on the methodology that was approved in December 2017.
  The quantities for 2019 reflect moving forward the historic data on which these are based, unless otherwise noted.
  Spreadsheets that contain the associated quantities for January through August of 2019 have been posted on the meeting page for September 12 PDCWG meeting.
ERCOT is seeking stakeholder feedback, for changes to the 2019 A/S Methodology.

## Slide 4
Divider Slide
Divider Slide (optional)
Regulation Service

## Slide 5: Regulation Service Methodology – 2019
The preliminary Regulation quantities for January 2019 thru July 2019 in subsequent slides have been computed using current methodology (2017 and 2018 five-minute net load variability) and updated Wind Adjustment tables.

## Slide 6: Wind Adjustment Table - 2019
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed Wind capacity.
  This table has been updated for 2019.

## Slide 7: Hourly Avg. Regulation Comparison

## Slide 8
Divider Slide
Divider Slide (optional)
Responsive Reserve Service

## Slide 9: Responsive Service Methodology (RRS) - 2019
The preliminary RRS quantities for January 2019 thru Aug. 2019 in subsequent slides have been computed using 2017 and 2018 system inertia conditions and RRS table updated in 2017.
In this slide deck to aid comparison with 2019 quantities, the 2018 RRS quantities have been adjusted to account for the responsiveness of hydro units under synchronous condenser mode, and the implementation of NPRR 815.

## Slide 10: RRS Jan 2019

## Slide 11: RRS Feb 2019
*.

## Slide 12: RRS Mar 2019

## Slide 13: RRS Apr 2019
*.

## Slide 14: RRS May 2019
*.

## Slide 15: RRS Jun 2019
*.

## Slide 16: RRS Jul 2019

## Slide 17: RRS Aug 2019

## Slide 18: Hourly Avg. RRS Comparison

## Slide 19
Divider Slide
Divider Slide (optional)
Non Spinning Reserve

## Slide 20: Non Spinning Reserve Methodology (NSRS) - 2019
The preliminary NSRS quantities for January 2019 thru Aug. 2019 in subsequent slides have been computed using current methodology and updated Wind Over-Forecast Error Adjustment tables.

## Slide 21: Wind Over-Forecast Error Adjustment Table - 2019
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed Wind capacity.
  This table has been updated for 2019.
Average hourly increase in Wind Forecast error per 1000 MW increase in installed Wind capacity = 40 MW
Notes: Average Hourly increase in 2018 = 45 MW

## Slide 22: NSRS Jan 2019
*1375 MW Floor in On-peak hours (HE 7 thru 22)

## Slide 23: NSRS Feb 2019

## Slide 24: NSRS March 2019

## Slide 25: NSRS Apr 2019

## Slide 26: NSRS May 2019

## Slide 27: NSRS June 2019

## Slide 28: NSRS July 2019

## Slide 29: NSRS Aug 2019

## Slide 30: Hourly Avg. NSRS Comparison

## Slide 31
Divider Slide
Divider Slide (optional)
Discussion

## Slide 32: RRS Table (Updated in 2017)
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.25:1 | 2.11:1 | 1.99:1 | 1.87:1 | 1.77:1 | 1.69:1 | 1.61:1 | 1.54:1 | 1.47:1 | 1.41:1 | 1.36:1 | 1.3:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5246 | 4916 | 4620 | 4361 | 4132 | 3927 | 3743 | 3576 | 3424 | 3285 | 3157 | 3040
*RRS (MW) | 3229 | 3162 | 3090 | 3039 | 2984 | 2920 | 2868 | 2815 | 2772 | 2726 | 2676 | 2643
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.26:1 | 1.22:1 | 1.17:1 | 1.14:1 | 1.1:1 | 1.07:1 | 1.04:1 | 1.01:1 | 1.00:1 | 1.00:1 | 1.00:1 | 1.00:1 | 1.00:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 2932 | 2831 | 2737 | 2650 | 2569 | 2492 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS (MW) | 2594 | 2550 | 2523 | 2477 | 2446 | 2408 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated with limit of 50% limit on LRs.
**Red font in table above identifies study scenario where RRS needed < 2300 MW. 2300 MW floor will be used in RRS requirement determination.
***Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest