## Slide 1
Calculation of Real-Time Combined Cycle Logical Resource Node Prices
Sai Moorty
Principal, Market Design and Analysis
QMWG
September 24, 2018

## Slide 2: Logical Resource Node (LRN)- Shift Factor and Dispatch
Type of aggregated Settlement Point – used only for Combined Cycle (CC) Train
LRN Shift Factor to a constraint is an aggregation of the individual physical Generation Resource Shift Factors of the Combined Cycle Generation Resource (CC configuration)
  Day-Ahead Market (DAM) : LRN shift Factor is the aggregation of HRL weighted Shift Factors of the individual physical Generation Resources in the CC configuration
  Real-Time Market (RTM) : LRN shift Factor is the aggregation of State Estimator output weighted Shift Factors of the individual physical Generation Resources in the CC configuration
Dispatch in DAM and RTM is governed by the On-Line CC configuration Energy-Offer Curve (EOC) and the LRN Shift Factor

## Slide 3: Logical Resource Node (LRN)- Shift Factor and Dispatch
meter1
CN-1
CN-2
CN-3
RN-1
RN-2
RN-3
EB-m1
Logical Resource Node
(Dispatch)
CT-1
CT-1
ST
BKR-1
BKR-2
BKR-3
BKR-5
BKR-4
BKR-6
BKR-7
BKR-8
BKR-9
BKR-10
BKR-11
CC Train
Rest of Grid
meter2
BKR-12
BKR-13
EB-m2

## Slide 4: Logical Resource Node (LRN) – Real-Time Settlements
Real-Time Energy Imbalance Payment or Charge at a Resource Node (6.6.3.1)
  At the LRN, the equation can be summarized as;
  At the LRN, there can be no PTP bids, DAM Energy-Only Offers/Bids, Self Schedules or Real-Time QSE-QSE trades
The Logical Resource Node Price, in the Real-Time Energy Imbalance Settlements is only used to determine the value of the Combined Cycle Resource Three Part Offer that was awarded in the DAM
  i.e, if the Combined Cycle Resource does not have any DAM three Part Offers, the Logical Resource Node Price does not come into play in Real-Time Settlements

## Slide 5: Logical Resource Node (LRN) – Pricing
Real-Time LRN price (LMP) computed from Shadow Prices and LRN Shift Factors: LRN_LMP_SF_AGG
  NPRR 890
  Consistency maintained with Base Point, Configuration EOC
    LRN Shift Factor used is the aggregation of the individual Generation Resources of the CC configuration – same as what is used to determine dispatch (Base Point)
Real-Time LRN price (LMP) computed as State Estimator output weighted LMP at the physical Resource Node of the CC configuration: LRN_LMP_RN_LMP_AGG
  More appropriate pricing, considering its sole use in Real-Time Energy Imbalance Settlements
  Aligns with the way Non Combined Cycle Generation Resource LMP is calculated
  Aligns with LRN LMP calculation in DAM
  Aligns with formula in Protocol (6.6.1.1 (2) (a)) prior to NPRR 890
  This is the ERCOT recommendation

## Slide 6: Logical Resource Node (LRN): Difference in Pricing Methods
Scenario # | Contingency with binding/overloaded constraint | Difference in LMP ?
1 | Constraint outside Gen site and Resource and Resource Node NOT disconnected | No Difference in LMP
2 | Constraint outside Gen site and Resource and Resource Node Both disconnected | Post NPRR 833 implementation: No difference in LMP Pickup Shift Factor applied to disconnected Resource Node LMP calculation
3 | Constraint outside Gen site and Resource disconnected and Resource Node NOT disconnected | If Pickup Shift Factor is significant, then LMP is not the same
4 | Constraint between Resource and Resource Node | LMP is not the same LRN_LMP_SF_AGG < LRN_LMP_RN_LMP_AGG

## Slide 7: History of Logical Resource Node (LRN) – Pricing
Nodal design/implementation phase prior to 2008
  No Protocol language describing specifics of LRN LMP calculation
  LRN LMP calculation based on Shadow Prices and LRN Shift Factor
    Driving force was making Base Point, EOC and LMP consistent
  Assumed that there would be no active constraints between Resource and Resource Node
  Assumed Pickup Shift Factor would be zero or insignificant
    ReCap: Pickup Shift Factor is the Shift Factor assigned to Generation Resource disconnected in Contingency
Just prior to Nodal Go-Live NPRR 228 described the LRN LMP calculations
  The formula described LRN LMP as HRL (DAM) or SE output (RTM) weighted Resource Node LMP
  Based on the assumptions above, this formula equivalent to LRN LMP computed from Shadow Prices and LRN Shift Factors

## Slide 8: History of Logical Resource Node (LRN) – Pricing
In 2015, it was discovered that DAM was calculating LRN LMP using Shadow Prices and HRL weighted average of the Resource Shift Factors rather than the HRL weighted Resource Node LMPs
  The LRN LMP was different due to a constraint between the Resource and the Resource Node
  ERCOT made system changes to both DAM (and RTM) to comply with Protocols
    ERCOT inadvertently used HRL for RTM instead of SE output
In 2018, ERCOT realized LRN LMP for RTM did not comply with protocol language
  Realized system changes were required to implement protocol language
  As short term fix,
    Reverted RTM LRN LMP to implementation prior to 2015 (Shadow Prices and LRN Shift Factor)
    Urgent NPRR to bring Protocols in alignment with system implementation

## Slide 9: System Changes: RT LRN Pricing as SE output weighted Aggregation of Physical Resource Node LMP
EMS Changes:
  In Real-time, transfer individual physical Generation Resource SE output (MW) for Combined Cycle Train to MMS
MMS Changes:
  For each SCED run, calculate LRN LMP as SE output weighted LMP at Resource Node of physical Generation Resources in the On-Line CC configuration

## Slide 10: Scenario 1: Constraint outside CC Gen Site
meter1
CN-1
CN-2
CN-3
RN-1
RN-2
RN-3
EB-m1
CT-1
CT-1
ST
BKR-1
BKR-2
BKR-3
BKR-5
BKR-4
BKR-6
BKR-7
BKR-8
BKR-9
BKR-10
BKR-11
CC Train
Rest of Grid
Logical Resource Node
(Dispatch)
LMP: LRN_LMP_SF_AGG
Logical Resource Node
LMP: LRN_LMP_RN_LMP_AGG
LRN_LMP_RN_LMP_AGG = LRN_LMP_SF_AGG
Over Load
meter2
BKR-12
BKR-13
EB-m2

## Slide 11: Scenario 2: Contingency Disconnects Both Resource and Resource Node – Post NPRR 833
meter1
CN-1
CN-2
CN-3
RN-1
RN-2
RN-3
EB-m1
CT-1
CT-1
ST
BKR-1
BKR-2
BKR-3
BKR-5
BKR-4
BKR-6
BKR-7
BKR-8
BKR-9
BKR-10
BKR-11
CC Train
Rest of Grid
Logical Resource Node
(Dispatch)
LMP: LRN_LMP_SF_AGG
Logical Resource Node
LMP: LRN_LMP_RN_LMP_AGG
LRN_LMP_RN_LMP_AGG = LRN_LMP_SF_AGG
Over Load
meter2
BKR-12
BKR-13
EB-m2

## Slide 12: Scenario 3: Contingency Disconnects Resource, Resource Node Connected
meter1
CN-1
CN-2
CN-3
RN-1
RN-2
RN-3
EB-m1
CT-1
CT-1
ST
BKR-1
BKR-2
BKR-3
BKR-5
BKR-4
BKR-6
BKR-7
BKR-8
BKR-9
BKR-10
BKR-11
CC Train
Rest of Grid
Logical Resource Node
(Dispatch)
LMP: LRN_LMP_SF_AGG
Logical Resource Node
LMP: LRN_LMP_RN_LMP_AGG
LRN_LMP_RN_LMP_AGG ≠ LRN_LMP_SF_AGG
Over Load
meter2
BKR-12
BKR-13
EB-m2

## Slide 13: Scenario 4: Constraint Between Resource and Resource Node
meter1
CN-1
CN-2
CN-3
RN-1
RN-2
RN-3
EB-m1
CT-1
CT-1
ST
BKR-1
BKR-2
BKR-3
BKR-5
BKR-4
BKR-6
BKR-7
BKR-8
BKR-9
BKR-10
BKR-11
CC Train
Rest of Grid
Over Load
Logical Resource Node
(Dispatch)
LMP: LRN_LMP_SF_AGG
Logical Resource Node
LMP: LRN_LMP_RN_LMP_AGG
LRN_LMP_RN_LMP_AGG > LRN_LMP_SF_AGG
meter2
BKR-12
BKR-13
EB-m2

## Slide 14
Questions?