## Slide 1
Resource Limit Calculator Logic
QMWG
Sean Chang, P.E.
Market Analysis
Alex Giarratano
Operations Analysis
9/24/2018

## Slide 2: Background
Low Sustainable Limit
At 5/2/2018 WMS, ERCOT presented a situation where operators performed a manual high dispatch limit (HDL) override due to a resource getting expected generation above high sustained limit (HSL)
At 6/4/2018 QMWG, ERCOT gave a tutorial on how this can happen due to a combination of static ramp sharing and regulation deployment
ERCOT proposed a dynamic ramp rate calculation at the 6/4/2018 QMWG and is bringing back analysis today

## Slide 3: Recap of Issue
Low Sustainable Limit
How can expected generation get above HSL?
Resource has regulation up and down responsibilities equal to a large percentage of its normal ramp rate
SCED deploys resource near its ancillary service (AS) limits (i.e. HASL)
Regulation is fully deployed to send resource well into AS region
Current static ramp sharing methodology means if a resource’s normal ramp rate is reserved for regulation, SCED can still use 2/7th of the normal ramp rate
Due to ramp sharing, SCED cannot dispatch resource back below HASL
Expected Generation = Base Point + Regulation Deployment + Expected Primary Frequency Response

## Slide 4: Proposed Methodology
Low Sustainable Limit
Current
SCED Down Ramp Rate =
= Normal Down Ramp Rate – Regulation Down Responsibility / 7
SCED Up Ramp Rate =
= Normal Up Ramp Rate – Regulation Up Responsibility / 7
Proposed
SCED Down Ramp Rate =
= Normal Down Ramp Rate
– [ (1 – Percentage of Up* Regulation Deployed )
* Regulation Down Responsibility / 7 ]
SCED Up Ramp Rate =
= Normal Up Ramp Rate
– [ (1 – Percentage of Down* Regulation Deployed )
* Regulation Up Responsibility / 7 ]
*Slightly modified from 6/4/2018 QMWG proposal

## Slide 5: Operational Benefits
Low Sustainable Limit
More accurate resource capabilities to allow for resolving congestion and ramp constraints
Better ability to dispatch according to price instead of being artificially limited by static 2/7th ramp rate
SCED correctly dispatches resource back below HASL and back above LASL and improves resource ability to follow regulation deployment

## Slide 6: Analysis
Low Sustainable Limit
Backcast performed form June 1, 2017 to May 31, 2018 with proposed methodology
Current methodology used as a benchmark
Results are conservative because backcast was performed for individual 5-minute intervals and not sequentially
Analyzed roughly 2,095,000 resource intervals where resource provided a regulation service

## Slide 7: Flagging Expected Gen > HSL
Low Sustainable Limit
Check if LDL + Reg. Depl. (T+5) was greater than HSL
Contribution from expected primary frequency response ignored
Remove intervals where 100% ramp sharing would still have flagged the interval
Proposed methodology still has flagged intervals due to non-sequential backcast or deviation from original base point
Methodology | # of Flagged Intervals
Current Methodology | 1,196 (0.05%)
Proposed Methodology | 405 (0.02%)

## Slide 8: Flagging LDL > HASL
Low Sustainable Limit
Check if LDL was greater than HASL
Remove intervals where 100% ramp sharing would still have flagged the interval
Proposed methodology still has flagged intervals due to non-sequential backcast or deviation from original base point
Methodology | # of Flagged Intervals
Current Methodology | 6,545 (0.31%)
Proposed Methodology | 3,195 (0.15%)

## Slide 9: Flagging SCED Backcast Ramp Violations
Low Sustainable Limit
Check if SCED and LFC asked for more ramp than resource’s ramp rate
  If Abs[BP + Reg. Depl. (T+5) – MW] > Ramp Rate and if BP equals LDL or HDL in proposed methodology, set BP to recalculated LDL or HDL
Increase is worst case scenario because it assumes base point with proposed methodology would have been at LDL or HDL and not the original base point
LFC deploys regulation independently of SCED dispatch instruction
Methodology | # of Flagged Intervals
Current Methodology | 17,848 (0.85%)
Proposed Methodology | 18,584 (0.87%)

## Slide 10: Flagging SCED Worst Case Ramp Violations
Low Sustainable Limit
Check if SCED and LFC asked for more ramp than resource’s ramp rate assuming base point was LDL or HDL
  If Abs[BP + Reg. Depl. (T+5) – MW] > Ramp Rate and if BP equals LDL or HDL in proposed methodology, set BP to recalculated LDL or HDL
Increase is worst case scenario because it assumes base point with proposed methodology would have been at LDL or HDL and not the original base point
LFC deploys regulation independently of SCED dispatch instruction
Methodology | # of Flagged Intervals
Current Methodology | 189,120 (9.0%)
Proposed Methodology | 208,444 (9.9%)

## Slide 11: Impacts to Base Point Deviation (±5% or 5 MW)
Low Sustainable Limit
Base point deviation impacts were examined with current and proposed methodology
Flag intervals where resource could not be within five percent or five MWs of Base Point + Regulation Instruction assuming its telemetered normal ramp rate
Simplified version of calculation was used:
  Only looks at every 5-minute interval instead of settlement interval
  Ignores exceptions such as frequency triggers
  If SCED asked for BP at LDL or HDL, then assume BP was at the newly calculated LDL or HDL in the proposed methodology
Methodology | # of Flagged Intervals*
Current Methodology | 1,316 (0.06%)
Proposed Methodology | 1,381 (0.07%)
  * Out of 2 million observed resource intervals providing regulation
Notes: The analysis flagged over 58,000 intervals when using this simplified methodology to look at whether a resource’s historical actual performance met the same criteria

## Slide 12: Impacts to GREDP (±8% or 8 MW)
Low Sustainable Limit
GREDP also examined with current and proposed methodology
Flag intervals where resource could not be within eight percent or eight MWs of Base Point + Regulation Instruction assuming its telemetered normal ramp rate
Simplified version of calculation was used:
  Again, ignores all of the exceptions
  Contribution from expected primary frequency response ignored
  If SCED asked for BP at LDL or HDL, then assume BP was at the newly calculated LDL or HDL in the proposed methodology
Methodology | # of Flagged Intervals*
Current Methodology | 555 (0.02%)
Proposed Methodology | 579 (0.02%)
  * Out of 2 million observed resource intervals providing regulation
Notes: The analysis flagged over 22,000 intervals when using this simplified methodology to look at whether a resource’s historical actual performance met the same criteria

## Slide 13: Impacts to Dispatchable Capacity
Low Sustainable Limit
HDL override on 2/10/2018
Chart: Change in HDL from Production SCED (MW)

## Slide 14: Impacts to Dispatchable Capacity
Low Sustainable Limit
Highest daily priced summer day in 2017 on 8/9/2017
Chart: Change in HDL from Production SCED (MW)

## Slide 15: Impacts to Dispatchable Capacity
$9,000 price spikes on 1/23/2018
Low Sustainable Limit
Chart: Change in HDL from Production SCED (MW)

## Slide 16: Conclusion
Low Sustainable Limit
Increasing ramp rates based on regulation deployments reduces potential for expected generation getting above HSL and increases flexibility for SCED to dispatch back below HASL
Minimal GREDP and BP Deviation impacts including reducing base point deviation charge when expected generation is above HSL
More accurate resource limits, improved SCED dispatch, and more optimal ramp sharing
Next Steps:
  Stakeholder Feedback
  Draft NPRR to use dynamic ramp rate calculation

## Slide 17
Low Sustainable Limit