## Slide 1
Review of Commercial Impacts of DC Tie Curtailments
QMWG
September 24, 2018
Market Analysis

## Slide 2: DC Tie Tag Curtailments – July 2018
There were 5 DC Tie Tag curtailment events
  3 were on the same day
  4 were due to local congestion
  1 was due to TO communication issue with DC Tie
Transmission watches were declared during all 5 events

## Slide 3: DC Tie Tag Curtailments – July 2018
Date | DC Tie | Curtailing Period | # of Tags Curtailed | Initiating Event | Curtailment Reason
7/17/2018 | DC-S | HE 19:00 – HE 22:00 | 3 | Local congestion | Post-contingency loss of the Bevo to Asherton 138 kV (SBEVASH8) overloads the Big Wells to Cotulla Sub 69 kV
7/23/2018 | DC-R | HE 01:00 – HE 03:00 | 1 | Local congestion | Post-contingency loss of Bentsen to Railroad (SBENRAI8) overloads South Mission to Railroad 138 kV
7/23/2018 | DC-R | HE 07:00 – HE 08:00 | 1 | Local congestion | Post-contingency loss of Bentsen to Railroad 138 kV (SBENRAI8) overloads South Mission to Railroad 138 kV
7/23/2018 | DC-R | HE 22:00 & HE 24:00 | 1 | Local congestion | Post-contingency loss of Bentsen to Railroad 138 kV (SBENRAI8) overloads South Mission to Railroad 138 kV
7/31/2018 | DC-R | HE 21:00 – HE 24:00 | 2 | TO communication issue with DC Tie | De-rated to 100MW

## Slide 4: 7/17/2018 Curtailment of DC-S
Chart: DC Tie Export (MW)
SBEVASH8: BIG_COTU_1 Shadow Price | 1006.4689 | 1804.0897 | 2800 | 0 | 0 | 339.4447 | 771.8825 | 761.96 | 695.0364 | 731.0602 | 693.4008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slide 5: 7/23/2018 Curtailment of DC-R
Contingency SBENRAI8 was never activated
DC tie was the only point with a hurting shift factor to the constraint
In HE22, curtailment had an impact on the SPOLPHA8:GCB_100_1 constraint in SCED
  violated prior to curtailment
  not binding after curtailment
  DC-R has about a 35% shift factor to the constraint

## Slide 6: 7/23/2018 Curtailment of DC-R
Chart: DC Tie Export (MW)
SPOLPHA8: GCB_100_1 Shadow Price | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 3500 | 3500 | 3500 | 3500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPOLPHA:GCB_100_1 was not the reason the tie was curtailed