## Slide 1
Bearkat Area Transmission Improvement
-- ERCOT Independent Review
TAC
September 26, 2018

## Slide 2: Overview
WETT submitted the economic-driven Bearkat Area Transmission Improvement project for Regional Planning Group review on August 15, 2017 that was estimated to cost $69.87 million.
  To address the transmission congestion resulting in restriction on the wind generation in the Bearkat area.
A total of 1,368 MW wind generation in the Bearkat area.

## Slide 3: Initial Option Evaluation
Alternatives | Capital Cost ($M)(1) | ROW (Mileage) | Annual PC Savings ($M)(2) | Annual PC Savings to Capital Cost Ratio | Meets Economic Criteria (15%) ?
Option 1 | 54.95 | 18.2 | 25.58 | 47 % | YES
Option 2 | 55.61 | 22.84 | 31.75 | 57 % | YES
Option 3 | 58.06 | 26.98 | 33.86 | 58 % | YES
Option 4 | 69.87 | 30.76 | 35.15 | 50 % | YES
Option 5 | 80.54 | 39.47 | 35.57 | 44 % | YES
Option 6 | 93.47 | 33.93 | 36.78 | 39 % | YES
Option 7 | 102.15 | 51.47 | 33.46 | 33 % | YES
Option 8 | 106.50 | 53.89 | 35.93 | 34 % | YES
Option 9 | 162.00 | 90 | 34.56 | 21 % | YES
Note:
(1). Based on initial capital cost estimate provided by WETT except Option 9 which was estimated by ERCOT.
(2). This economic analysis did not include the Lubbock Integration project.
All nine options met the ERCOT economic criteria

## Slide 4: Summary of Transfer and NPV Results
Option | Capital Cost ($M)(1) | Export Limit Out of Bearkat (MW) | ROW (Miles) | Annual Production Cost Savings ($M)(2) |  |  | Net Societal Benefit (HOG = $3.32) (3) |  | Net Societal Benefit ( Low Gas = $2.99) |  | Net Societal Benefit ( Reference = $4.42) | 
 |  |  |  | HOG ($3.32) | Low Gas ($2.988) | High Gas ($4.42) | 15 Year Net Savings ($M) | 30 Year Net Savings ($M) | 15 Year Net Savings ($M) | 30 Year Net Savings ($M) | 15 Year Net Savings ($M) | 30 Year Net Savings ($M)
Option 1 | 54.95 | 1,015 | 18.2 | 25.58 | 22.46 | 36.05 | 190.6 | 306.0 | 159.7 | 261.1 | 294.0 | 456.7
Option 2 | 55.61 | 1,619 | 22.84 | 31.75 | 25.77 | 40.75 | 250.8 | 394.0 | 191.7 | 308.0 | 339.7 | 523.5
Option 3 | 58.06 | 1,618 | 26.98 | 33.86 | 26.84 | 44.86 | 268.9 | 421.6 | 199.5 | 320.6 | 377.6 | 579.9
Option 4 | 69.87 | 1,528 | 30.76 | 35.15 | 27.56 | 52 | 268.3 | 426.8 | 193.3 | 317.6 | 434.7 | 669.3
Option 5 | 80.54 | 1,359 | 39.47 | 35.57 | 27.88 | 49.31 | 260.3 | 420.8 | 184.3 | 310.1 | 396.1 | 618.5
Option 6 | 93.47 | 1,659 | 33.93 | 36.78 | 29.47 | 52.12 | 257.7 | 423.6 | 185.4 | 318.4 | 409.2 | 644.3
Option 7 | 102.15 | 1,594 | 51.47 | 33.46 | 26.95 | 48.6 | 215.0 | 366.0 | 150.7 | 272.3 | 364.6 | 583.9
Option 8 | 106.5 | 1,402 | 53.89 | 35.93 | 29.97 | 51.8 | 234.5 | 396.6 | 175.6 | 310.8 | 391.3 | 625.0
Option 9 | 162 | 1,388 | 90 | 34.56 | 31 | 51.98 | 158.2 | 314.1 | 123.0 | 262.9 | 330.3 | 564.8
(1). Based on initial capital cost estimate provided by WETT except Option 9 which was estimated by ERCOT.
(2). This economic analysis did not include the Lubbock Integration project.
(3) The project cost of each option was considered to be the capital cost of the project for purposes of this analysis(2)

## Slide 5: Selected Short-Listed Options
ERCOT short-listed Options 2, 3, 4, and 6 were selected for the following reasons:
  Both Option 3 and Option 4 provide the best overall net societal benefits while providing relatively high transfer limits
  Option 6 was selected as it also provides an overall net societal benefit better than other options and is estimated to provide the best transfer capability among all options
  Option 2 was selected because it is one of the least cost 345 kV options and provides a high transfer limit, while providing relatively good overall net societal benefits

## Slide 6: Short-Listed Option Evaluation Results
Short-listed options were further analyzed with the following updates:
  Included Lubbock integration project in the economic study case
  Updated capital cost estimates provided by TSPs
Option | Updated Capital Cost ($M) | Export Limit Out of Bearkat (MW) | ROW (Miles) | Annual Production Cost Savings with LP&L ($M) | Annual PC Savings to Capital Cost Ratio | Net Societal Benefit with Updated Costs and LP&L (HOG = $3.32) | 
 |  |  |  | HOG ($3.32) |  | 15 Year Net Savings ($M) | 30 Year Net Savings ($M)
Option 2 | 53.11 | 1,619 | 22.84 | 30.94 | 58% | 245.62 | 385.19
Option 3 | 53.26 | 1,618 | 26.98 | 31.70 | 60% | 252.97 | 395.97
Option 4 | 68.62 | 1,528 | 30.76 | 32.44 | 47% | 242.89 | 389.24
Option 6 | 103.32 | 1,659 | 33.93 | 33.04 | 32% | 209.56 | 358.61

## Slide 7: Other Studies
According to Protocol Section 3.22.1.3(2), ERCOT performed a SSR vulnerability assessment with Option 3 and the results showed no SSR vulnerability for any existing Generation Resources or Generation Resources satisfying Planning Guide Section 6.9 conditions for inclusion in the planning models at the time of this study.
ERCOT determined that generation addition sensitivity analysis per PG 3.1.3(4)(a) and load scale impact sensitivity analysis PG 3.1.3.(4)(b) are not necessary because of the following reasons:
  There are no new generation with signed Interconnection Agreement that did not meet PG 6.9 requirements in the Bearkat area.
  Any new generation to the existing system in the Bearkat area will aggravate the congestion issues.
  Load scaling was not used to create the economic cases used in the study

## Slide 8: ERCOT Recommendation
Based on the ERCOT Independent Review, ERCOT will recommend the Board endorse Option 3 to resolve the congestion in the study region.
  Adding a new 345-kV bay at the Longshore 345-kV station,
  Adding a new 345-kV bay at the Bearkat 345-kV station, and
  Constructing a new 345-kV single-circuit line on a double-circuit capable structure (~ 27 mile) from Bearkat station to Longshore station
Estimated Capital Cost: $53.26 million

## Slide 9: Option 3
?

## Slide 10
Appendix

## Slide 11: Appendix – Transmission Option 1 (Presented by WETT at 08/22/2017 RPG)

## Slide 12: Appendix – Transmission Option 2 (Presented by WETT at 08/22/2017 RPG)

## Slide 13: Appendix – Transmission Option 3 (Presented by WETT at 08/22/2017 RPG)

## Slide 14: Appendix – Transmission Option 4 (Presented by WETT at 08/22/2017 RPG)

## Slide 15: Appendix – Transmission Option 5 (Presented by WETT at 08/22/2017 RPG)

## Slide 16: Appendix – Transmission Option 6 (Presented by WETT at 08/22/2017 RPG)

## Slide 17: Appendix – Transmission Option 7 (Presented by WETT at 08/22/2017 RPG)

## Slide 18: Appendix – Transmission Option 8 (Presented by WETT at 08/22/2017 RPG)

## Slide 19: Appendix – Transmission Option 9 (Additional Option Tested by ERCOT)

## Slide 20: Appendix – Updated Capital Cost Estimates

## Slide 21: Previous RPG presentations
Wind Energy Transmission Texas (WETT) submitted Bearkat Area Transmission Improvements project for Regional Planning Group review. This is a Tier 1 project that is estimated to cost $ 69.87 million. http://www.ercot.com/calendar/2017/10/19/108887-RPG
ERCOT provided scope updates and study assumptions at the February RPG. http://www.ercot.com/calendar/2018/2/27/138675-RPG
ERCOT presented preliminary results and future steps at the April RPG. http://www.ercot.com/content/wcm/key_documents_lists/138684/Bearkat_Update_04_24_2018_RPG.pdf
ERCOT presented results from weather sensitivity and outage probability analysis at the May RPG. http://www.ercot.com/content/wcm/key_documents_lists/138688/Bearkat_Update_05_22_2018_RPG.pdf
ERCOT presented an update on study results with Kontiki wind modeled in base cases. http://www.ercot.com/content/wcm/key_documents_lists/159769/Bearkat_Update_07_25_2018_RPG.pdf