## Slide 1
ERCOT 2018 UFLS Survey Results
Daniel Sanchez
Compliance Analyst

## Slide 2: Background on the ERCOT UFLS Survey and Requirements
ERCOT coordinates and conducts the survey with TDSPs. The survey serves to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event. The table below, taken from the ERCOT Operating Guide 2.6.1(1) Requirements for Under-Frequency Load Shedding, lists the required load shed amounts:
Operating Guide 2.6.1 (2)
With the assistance of applicable Transmission Service Providers (TSPs), ERCOT will, prior to the peak each year, survey each Distribution Service Provider’s (DSP’s) compliance with the automatic Load shedding steps above, and report its findings to the Technical Advisory Committee (TAC). For minimum compliance, DSPs are obligated to meet the prescribed percent values at all times.
Frequency Threshold | Load Relief
59.3 Hz. | 5% of the ERCOT System Load (Total 5%)
58.9 Hz. | An additional 10% of the ERCOT System Load (Total 15%)
58.5 Hz. | An additional 10% of the ERCOT System Load (Total 25%)

## Slide 3: Timeline of the 2018 ERCOT UFLS Survey
Below is a timeline reflecting the survey dates and activities:
Date | Activity
Thursday, March 15th | ERCOT announcement of survey timeline to the OWG.
Monday, April 2nd | Market Notice sent by ERCOT Client Services to TDSP Authorized Representatives.
Thursday, May 10th | Date and time of survey.
Tuesday, June 12th | Survey results due to ERCOT.
Wednesday, July 18th | Survey results to be reported to the OWG.
Thursday, August 9th | Survey results to be reported to the ROS.
Thursday, August 30th | Survey results to be reported to the TAC.

## Slide 4: Results of the 2018 ERCOT UFLS Survey
The overall results of the 2018 UFLS survey are reflected below:
All TDSPs successfully met the individual 5/10/10 requirements.
The ERCOT load at the time of the survey was 43,252 MW. In comparison, the 2017 survey overall total was 34.1% at 42,510 MW of load.
(Note—NOGRR178 is still in progress for potential changes to the 2019 survey.)
Frequency Response Block | Minimum Requirement | Survey Measurement
Block 1 response at 59.3 Hz. | 5% | 7.9%
Block 2 response at 58.9 Hz. | 10% | 12.8%
Block 3 response at 58.5 Hz. | 10% | 12.7%
Total | 25% | 33.4%