## Slide 1
RARF v5.4 GIC Data Requirements
Resource Integration Workshop
Ed Geer, P.E.
Lead Network Model Engineer
Resource Integration
September 28, 2018

## Slide 2: RARF v5.4 GIC Data Requirements
What GIC (Geomagnetically-Induced Current) model data is required on RARF v5.4?
  Station data
  Line data
  Series Device data
  Shunt Reactor data
  Transformer data
When is the RARF GIC data required?
  60 days after meeting Planning Guide 6.9 (1) requirements -
    Screening Study / FIS data provided by Interconnecting Entity (IE)
    Signed SGIA, notice to proceed with construction and financial security
    Air permit and water supply, if required

## Slide 3: RARF v5.4 GIC Data Requirements
GIC data - Transmission Form as specified by RARF Glossary – Planning Model column
Station tab –
  Latitude of Center of Station (decimal degrees (N)) - The geographic coordinate that specifies the north-south position of the station provided in decimal degrees
  Longitude of Center of Station (decimal degrees (W)) - The geographic coordinate that specifies the east-west position of the station provided in decimal degrees
  Station DC Grounding Resistance - Enter the DC resistance in Ohms of the grounding network to remote earth for this station. If the station has a ground grid that is or may be connected to the TSP ground grid, coordination with your TSP is needed.
Line Data tab - DC Resistance (Ohms/Phase) - Enter the DC Resistance in Ohms per phase of the line. [adjusted to 50°C]
Series Device Data tab – DC Resistance (Ohms/Phase) - Enter the DC Resistance in Ohms per phase of the Series Device [adjusted to 50°C]

## Slide 4: RARF v5.4 GIC Data Requirements
Capacitor and Reactor Data tab –
  Coil DC resistance (Ohms/Phase) - Enter the DC resistance in Ohms/phase for grounded shunt reactor coils (enter "99999" for ungrounded shunt reactors and all shunt capacitors). [adjusted to 75°C]
  Grounding DC resistance (Ohms) - Enter the DC resistance in Ohms for the grounding device for grounded shunt reactors (for solidly grounded shunt reactors, enter 0, or enter "99999" for ungrounded shunt reactors and for all shunt capacitors).
Transformer Data tab –
  Transformer Test Report Attached? (Y/N) - Is the Transformer test report attached to this Resource Registration?
  DC Resistance of Winding 1 (Ohms/Phase) - Using manufacturer's data, enter the DC resistance of the Primary/high voltage winding (or for autotransformers, the series winding). [adjusted to 75°C]

## Slide 5: RARF v5.4 GIC Data Requirements
Transformer Data (continued) –
  DC Resistance of Winding 2 (Ohms/Phase) - Using manufacturer's data, enter the DC resistance of the Secondary/low voltage winding (or for autotransformers, the common winding). For physical three-winding transformers modeled as three 2-winding transformers, enter "99999"for each transformer row. [adjusted to 75°C]
  GIC Blocking device on Winding 1 (Y/N) - Answer Yes or No whether a Geomagnetically-Induced Current blocking device exists on the Primary/high voltage winding (or for autotransformers, the series winding).
  GIC Blocking device on Winding 2 (Y/N) - Answer Yes or No whether a Geomagnetically-Induced Current blocking device exists on the Secondary/low voltage winding, (or for autotransformers, the common winding). For physical three-winding transformers modeled as three 2-winding transformers, select "N" for each transformer row.

## Slide 6: RARF v5.4 GIC Data Requirements
Transformer Data (continued) –
  Vector Group Identifier (List) - Manufacturer-supplied alphanumeric identifier specifying vector group based on transformer winding connections and grounding. For physical three-winding transformers modeled as three 2-winding transformers, enter the same Vector Group Identifier for each transformer row.
  Transformer Core Design Type (List) - Manufacturer-supplied Transformer Core Design Type (Three Phase shell Form, Unknown, 3@Single Phase (separate cores), Three Phase 3-Legged Core Design, Three Phase 5-Legged Core Design, Three Phase 7-Legged Core Design). For physical three-winding transformers modeled as three 2-winding transformers, enter the same Transformer Core Design Type for each transformer row.
  K Factor (Number) - Value supplied by transformer manufacturer. If data is unavailable from the manufacturer, enter 0. For physical three-winding transformers modeled as three 2-winding transformers, enter the same K Factor for each transformer row.

## Slide 7: RARF v5.4 GIC Data Requirements
Transformer Data (continued) –
  Winding 1 Grounding DC Resistance (Ohms) - Enter the Primary/high voltage winding Grounding DC Resistance in Ohms for any grounding device, (for a solidly grounded winding, enter 0, enter "99999" for ungrounded).
  Winding 2 Grounding DC Resistance (Ohms) - Enter the Secondary/low voltage winding Grounding DC Resistance in Ohms for any grounding device, (for a solidly grounded winding, enter 0, enter "99999" for ungrounded). For physical three-winding transformers modeled as three 2-winding transformers, enter "99999" for each transformer row.
  Transformer Model - Enter 0 except for a phase-shifting transformer, which should be entered as a 1. For physical three-winding transformers modeled as three 2-winding transformers, enter the same model for each transformer row.

## Slide 8: RARF v5.4 GIC Data Requirements
Transformer Test Data tab –
  Embed the Transformer Test Data Report (at the time it becomes available) –
    winding DC resistance in Ohms per phase
    Vector Group Identifier
    Transformer Core Design Type, if available
    K Factor, if available
    positive and zero sequence resistance and reactance data
    winding voltages
    tap information
    on-load tap changing capability
    ratings

## Slide 9: RARF v5.4 GIC Data Requirements
Where to find additional information and helpful references –
  Planning Geomagnetic Disturbance Task Force – Key Documents http://www.ercot.com/committee/pgdtf
    GIC Application Guide 2013 – Approved
    GIC System Model Procedure Manual ROS Approved 11118
    PGDTF GIC Model User Guide 2 15 2018
  PDCWG Meeting – May 10, 2017 - GIC System Model Data Workshop presentations
    01 04 GIC System Model Workshop Material OU 05102017
    02 Transformer Resistance Workshop Presentation 05162017
    03 AEPs Ground Grid Resistance Measurement Procedure 05102017

## Slide 10: RARF v5.4 GIC Data Requirements
Other helpful references –
  RARF Glossary –
    http://www.ercot.com/mktrules/guides/resourcereg/library.html
  Frequently Asked Questions - RARF v5.4 in the RARF package posted at the below link
    http://www.ercot.com/services/rq/re/index.html
    Resource Asset Registration Forms

## Slide 11: RARF v5.4 GIC Data Requirements
Questions or comments?