## Slide 1
Resource Integration Workshop
ERCOT
Jay Teixeira
September 28, 2018

## Slide 2: Quarterly Stability Assessment (QSA)
Planning Guide 5.9
Next Deadline for QSA
If a GINR is not included in QSA, its Initial Synchronization date will be automatically delayed to the next quarter
All-Inclusive Generation Resource Initial Synchronization Date | Last Day for an IE to meet prerequisites as listed in paragraph (4) below | Completion of Quarterly Stability Assessment
Upcoming January, February, March | Prior August 1 | End of October
Upcoming April, May, June | Prior November 1 | End of January
Upcoming July, August, September | Prior February 1 | End of April
Upcoming October, November, December | Prior May 1 | End of July

## Slide 3: Quarterly Stability Assessment (QSA)
Planning Guide 5.9, Quarterly Stability Assessment
Issue’s seen in the QSA that had May 1, 2018 deadline
  10 day comment period for FIS
    Needs to be complete before QSA deadline
    TSPs need to plan for it
  Dynamic data validation
    Dependent on FIS Stability study
    Need to meet PG 6.9 15 to 30 days prior to QSA deadline

## Slide 4: RIOO-GINR Application Go-Live

## Slide 5: What Happened?
Application was ready from a functional perspective
ERCOT Security does a security assessment on every new application.
  Issues have to be identified and resolved prior to allowing external access to the application
  This application is different from most
    Allows non-registered entities to create accounts and upload files with only an email address
    Other applications are restricted to Market Participants that are considered to be more vetted

## Slide 6: Dates
Internal Go-Live occurred on August 31, 2018
  Used by RI to track INRs
  Used for GIS Report
  Used for Monthly Project Update
Training will be given at November 30, 2018 workshop
External Go-Live target date December 11-13, 2018
  IE functionality except for payment
  TSP functionality
External Go-Live with payment around March 2019

## Slide 7: Masked Dates
Certain Dates and Periods will be “masked” so that they cannot be selected for
  Energization Date
  Synchronization Date
  Commercial Operation Date
Dates will be ERCOT Holidays
Periods will be
  Week of Thanksgiving
  Week between Christmas and New Years Day

## Slide 8: PGRR Language Review This Workshop

## Slide 9: Miscellaneous Updates 3rd Review
Main Power Transformer (MPT) – transformer in a station with generation resources where voltage is transformed from a voltage lower than 60 kV to a voltage higher than 60 kV. For thermal generation resources, also known as a Generation Step-Up (GSU) transformer.

## Slide 10: Miscellaneous Updates 3rd Reivew
Added to 5.2.1(4) – that COD date can be changed after submission (5.2.1 (3) in greybox)
  Re-powers not subject to 15 month rule?
Edited 5.4.2.1(6) during meeting to clarify FIS scope and study agreement requirements
Added 5.4.8(1) – requirement that separate FIS study element reports be created for posting for the IE – Some TSP have problem with separating SS, SC, and Facility but can separate these 3 from the dynamic.

## Slide 11: Miscellaneous Updates 3rd Reivew
Added 5.7.1(4)(b)(vi) – to submit Reactive Study prior to Stability study and data requirements for TSP to give to IE
  Quick fault current study different than SC study done later
  Discuss at next meeting
Reworded 5.9(4)(b) – to not add new requirement but make suggestion that model be submitted 30 days prior to QSA

## Slide 12: Under Discussion This Workshop

## Slide 13: RARF Guidelines for Inverter-Based Resources
Inverter Details
  “MW Rating for this model of Inverter” should reflect unity power factor (i.e. the MVA rating for the inverter)
Unit Info
  “Name Plate Rating” = (number of inverters) x (MVA rating of inverter)
  “Real Power Rating” and “Reactive Power Rating” should be based on “Name Plate Rating” as defined above assuming a reasonable power factor (0.9 – 0.95)
  These values represent the aggregate resource as modeled at the medium voltage bus
  Estimated losses should not be included prior to detailed collector system design

## Slide 14: Planning Geomagnetic Disturbance Task Force
Task Force created in October 2014 to create planning models to comply with NERC Standard TPL-007-1
NERC TPL-007-1 created to satisfy FERC Order No. 779
Multiple market rules changes in support of PGDTF
  PGRR046 - Addition of Geomagnetically Induced Current (GIC) Model Building Requirements
  PGRR057 - Responsibilities for Performing Geomagnetic Disturbance (GMD) Vulnerability Assessments
  RRGRR009 - Adding Voltage Limit Sets, Relay Loadability, MLSE, and GMD Data
  RRGRR015 - Additional Guidance for Transformer and Station Data

## Slide 15: FIS Data Requirements for Kick-Off Meeting
Presentation by:
  Mike Juricek

## Slide 16: GIC Data Submittal Requirements
Presentation by:
  Ed Geer

## Slide 17: Up Next Discussion next Workshop

## Slide 18: PGRR’s Submitted

## Slide 19: PGRR’s Submitted
PGRR062 - Updates to Generation Interconnection or Change Request (GINR) Process – BOD approved August 7, 2018
PGRR066 - Interconnection Request Cancellation and Creation of Inactive Status – language review at Sept 18, PLWG, next Oct 11, ROS
PGRR067, NPRR882 – Re-powering Procedures – language review at Sept 18, PLWG, next Oct 11, ROS

## Slide 20: Back Log

## Slide 21: Possible Changes to Interconnection Process Projects must have a unique name
Interconnection requests must include a name that is not in use anywhere else in the ERCOT system and not too similar to any other name
  Use ERCOT Planning Data Dictionary and GIS Report
  ERCOT Operations uses NMMS model name but REs and TSPs may use different name. It is critical that equipment names are unique, easy to spell, and pronounce, and used by all
  Once a project name is acceptable to ERCOT it will not be changed

## Slide 22: Possible Changes to Interconnection Process Propose Fee Increase for Project Determination
Screening Study Advanced. This option consists of:
  appropriate case(s)
  one POI will be studied
  a set of transmission projects to allow full output will be determined
  current fee schedule price + $4,000
  completed in 90 days
  Normal Tracking and Coordination
Need ERCOT advice on how to proceed

## Slide 23: Other contact information
GINR@ercot.com - still used for INR activity
ResourceIntegrationDepartment@ercot.com is distribution list for Resource Integration department

## Slide 24: Questions?
Thank you!

## Slide 25: The following are old slides for reference only

## Slide 26: MW Output of Proposed Resources
The MW size that is proposed by a new All-Inclusive Generation Resource is at the generator terminals entering the low side of the gsu/main transformer. – 5.1.1(a)
The change in MW size that triggers GINR applicability should be based on Seasonal Net Max Sustainable Rating in latest RARF – 5.1.1(b)(i)

## Slide 27: Possible Changes to Interconnection Process Miscellaneous
IE/TSP agreement on FIS scope - Clock starts ticking towards 60 day deadline at FIS Kickoff Meeting - 5.4.2.1 (6)
Minimum COD date to accept in a GINR application
  18 to 24 months typical time frame to go from application to commissioning – 5.2.1(4), changed to 15 months
Alter PG section 5.9 Quarterly Stability Assessment
  Add new deadline to meet PG 6.9 Addition of Proposed Generation to the Planning Models so that models can be validated prior to last day to meet prerequisites – 5.9(4)(a) and 5.9(4)(c) – changed to provided data

## Slide 28: Possible Changes to Interconnection Process Projects cannot be split
Aug 30: Developers will no longer be able to sub-divide projects into phases with same or different synchronization dates
  Projects can be decreased in size
  Additional projects can be submitted at the same POI
  The current practice causes confusion and time-consuming documentation and reporting problems
  Dec 18: Comment: Not liked by IE’s as they divide due to power purchase agreements.
  Further comment: Can split but need to pay fees for all INR’s created by split

## Slide 29: Continued from previous slide Splitting One INR into multiple INRs
When an INR is split, the original INR MW size is modified to show the amount that continues to use original INR number with a COD.
  FIS study will complete all studies using new MW amount and COD if not already done. If done, TSP certifies new studies are not required
  SSR study (if required and not done) will be done for new MW size and COD
  New Screening Study Fee not needed for this INR
  TSP charges for all FIS work done before and after split
  New NTP and Financial Security needed, changed to not needed

## Slide 30: Continued from previous slide Splitting One INR into multiple INRs
A new INR number will be created for each remaining piece with designated MW size and COD.
  Screening Study Fee will need to cover difference of original single INR fee that was paid versus cost of all new INRs created by split
  FIS Fee will not be needed if paid in original INR
  FIS study will be done using new MW Size and COD or TSP certifies not needed
  SSR study (if required) will be done for each new INR created by split
  TSP charges for additional work for each INR created by split
  New NTP and Financial Security needed for each INR created by split
  Must be done at the same time, no MWs left over for future use
  MW’s not used in split will be lost

## Slide 31: Continued from previous slide Splitting One INR into multiple INRs
ERCOT Security Screening Study (Not Refundable) | NA | A preliminary study of the impacts of a proposed generation plant conducted by ERCOT staff - $5,000 (less than or equal to 150MW) $7,000 (greater than 150MW)
200
100
100
+
$7000
$5000
$5000
+
=
$10000
Splitting a 200 MW INR into 2 100 MW INRs will cost an additional $3000

## Slide 32: TBD Status
  ERCOT will move INR with no communication to a new status, tentatively called TBD Status.
  INR in TBD Status will be calculated separately in GIS Reports.
  INR in TBD Status will have to pay INR fees again to move forward, keeping the INR number
    FIS studies may have to be updated or redone
    RARF data may have to be updated
  INR in TBD Status can cancel their request for no cost
  INR in TBD Status for 60 days will follow cancellation process
  PGRR to define this in 2018

## Slide 33: Possible Changes to Interconnection Process Sale of project before commercial operation
Seller informs ERCOT of sale, identifies buyer, and provides contact information
ERCOT asks buyer to confirm by submitting an updated RARF including contacts.
ERCOT places project into TBD status until RARF confirmation received.
ERCOT will cancel any project left in TBD status for more than 60 days.
Project clock continues to click while in TBD status

## Slide 34: Possible Changes to Interconnection Process Developers must reply to ERCOT requests
When ERCOT staff request additional or updated information about a project, the developer shall either answer in full or acknowledge the request within 10 days and commit to answering by a future date. PG 5.3.2(1). This request will be done by email for documentation purposes.
INR will be put in TBD Status after 10 days
ERCOT will cancel any project left in TBD status for more than 60 days.

## Slide 35: Possible Changes to Interconnection Process Biannual Attestations as Proof of Life and Communication
Bi-Annual RARF attestations are required by PG 5.3.2 (3)
  There are numerous INR projects that have not had action in years
  These INRs need to be cancelled to keep project list reflective of active projects
  Attestations will alert ERCOT to projects not active or where communication avenues (email, phone) are not correct
  New GINR app will provide attestation (slide 21).
  Separate attestation from RARF submittal
  Move GINR that has missed an attestation to TBD status if communication attempts fail

## Slide 36: Possible Changes to Interconnection Process Temporary and Permanent POI in same INR
Aug 30: No longer allow temporary POI and permanent POI studies in same INR. These will be submitted as separate INRs. Currently allowed by PG 5.4.2.2 (2) if agreed by IE and TSP
  Different POI quite often have very different power flow results
  Leads to situation where a GTC is not needed for temporary POI but is needed for permanent POI
  Comment: need for Temp POI not known until FIS underway
Dec 18: For further discussion: Temp and Perm POI at the same physical location can be in same INR if at the same location.
  If not at same location, then separate into two INRs and temp POI must have breakers and built to possibly be permanent.
  Temp and perm POI in same INR, 16.5 requirements must be met for entire INR (both temp and perm POI) to synchronize at temp POI

## Slide 37: Continued from Previous Slide Temporary and Permanent POI in same INR
Having one INR number refer to different POI’s and/or different COD’s is not practical and difficult to track
Once a Temporary POI is decided upon, a new INR number will be created using “xxxx” = “9zzz” (format yrINRxxxx) where “zzz” is the last three digits of original INR number
  Remainder of activity only for temporary POI and its corresponding COD.
  FIS study will complete short circuit and stability studies using only temp POI
  SSR study (if required) will only be for temp POI
  TSP charges for this portion of FIS
  Facility, NTP and Financial Security needed to cover both temporary and permanent POI
  Temp POI use will be granted for up to 26 months
    Extensions only granted for TSP requests

## Slide 38: Continued from Previous Slide Temporary and Permanent POI in same INR
Having one INR number refer to different POI and/or different COD is not practical and difficult to track
The original INR number will be used for the Permanent POI and its corresponding COD.
  Screening Study Fee will not be needed if already paid
  FIS Fee will not be needed if already paid
  FIS study will complete all FIS studies required by TSP using only perm POI and COD not already completed
  SSR study (if required) will be done for perm POI
  TSP can charge for additional work for this part of FIS

## Slide 39: Continued from Previous Slide Temporary and Permanent POI in same INR
ERCOT expressly reserves the right to withdraw its approval of continued operations at the temporary Point of Interconnection or take other appropriate action at any time in the future, should ERCOT determine, in its sole discretion, that the temporary Point of Interconnection is negatively impacting reliability of the ERCOT system or is in violation of any of ERCOT’s operational standards.

## Slide 40: Re-Power GINR
5.1.1 Applicability
(1) The requirements in this Section 5, Generation Resource Interconnection or Change Request, are applicable, to the following:
(a) Any Entity proposing a new All-Inclusive Generation Resource, including a storage device, with an aggregate power output (gross Generation Resource output minus auxiliary Load directly related to the Generation Resource) of ten MW or greater, planning to interconnect to transmission in the ERCOT System; or
(b) Resource Entities that are seeking to:
(i) Upgrade the summer or winter Net Dependable Capability of an All-Inclusive Generation Resource by ten MW or greater within a single year;
(ii) Re-power an All-Inclusive Generation Resource of ten MW or greater; or
(iii) Change or add a Point of Interconnection (POI) of an All-Inclusive Generation Resource of ten MW or greater

## Slide 41: Re-Power GINR
  ERCOT has seen many of these in 2017
  The term “Re-Power” in PG not related to “Repowering” or “Repowered Facility” definitions in ERCOT Protocols or PUCT rules
  GINR must be submitted
    Screening Study required if MW increase is 10 MW or more
    Additional information for reactive, SSR, and VRT capability compared with pre re-power equipment helpful to determine which FIS studies need to be done
    Stability model submission or detailed comparison with pre re-power equipment model necessary to determine if FIS stability study needs to be done
    Part 2 and Part 3 necessary although facility has already synchronized
      Need to check model and PFC, Voltage Control, Reactive Capability and AVR
  PGRR to clarify this information in 2018
Notes: Part 2 necessary to check model (may need to re-aggregate if wind) and telemetry and inform PMU requirements

## Slide 42: INR Cancellation Process
Current Process
    ERCOT sets COD back 1 year when it determines current COD is unlikely given current status and notifies IE
      Occasionally, IE gets caught up and COD can move back toward original COD
      IE gives ERCOT new COD date further in the future
      IE notifies ERCOT to cancel the request
    If there is no response from an IE after an ERCOT request, INR cancellation will be initiated
ERCOT will initiate PGRR to define a formal cancellation process in 2018

## Slide 43: Possible Changes to Interconnection Process Temporary Taps Not Allowed
POIs consisting of a non-breakered tap to an existing line will not be accepted in future FIS reports
  Change will apply to all projects where the FIS has not been approved by ERCOT effective May 31, 2018
  Going forward, ERCOT will not approve FIS reports for this type of configuration
  Need for exit strategies will be determined for existing non-breakered POIs with Resource Commissioning Date after January 1, 2013

## Slide 44: Possible Changes to Interconnection Process Temporary Taps Not Allowed, Market Notice sent June 14, 2018

## Slide 45: Possible Changes to Interconnection Process Temporary Taps Not Allowed, Market Notice sent June 14, 2018

## Slide 46: Possible Changes to Interconnection Process Temporary Taps Not Allowed, Market Notice sent June 14, 2018

## Slide 47: Possible Changes to Interconnection Process Temporary Taps Not Allowed, Market Notice sent June 14, 2018

## Slide 48: Possible Changes to Interconnection Process Temporary Taps Not Allowed, Additional Information
Any planned FIS containing a hard tap that was submitted and approved before May 31, 2018, but isn’t energized, can proceed with the hard tap plan, but still needs to have an exit strategy

## Slide 49: Possible Changes to Interconnection Process Miscellaneous
Language to require IE submit Reactive Study prior to TSP start of FIS Stability Study
  IE need SC info from TSP to do reactive study
  TSP do VRT first and need reactive study
  Reactive Study can be done at same time as steady state study
  How can TSPs provide SC info
    Provide after study scope agreement is signed

## Slide 50: Possible Changes to Interconnection Process Miscellaneous
Tightening of timeline for TSP to complete FIS studies
  Dependent on IE submittal of necessary data for each stage of FIS
    Many data problems
    TSP put timeline in study scope
    TSP report minimum 180 days under ideal conditions
Alter PG section 5.4.8 (8) from “before meeting Section 6.9” to “before Initial Synchronization”.
  Removed from PGRR062, added to PGRR066

## Slide 51: Screening Studies
Screening Study Responsibility to RI group
Mario Hayden to RI group
+2 Contractors
+ 2 contractors to do SS

## Slide 52: Possible Changes to Interconnection Process Propose new fee structure
Propose a new fee structure to make sure that INRs are serious propositions and not fishing.
  Overloads ERCOT staff with extraneous studies
  More attention needs to be paid to screening study results where generation deliverability is shown to affected
  Graduated scale (inc) for subsequent INR requests?
  Higher fee for INR to voltage less than 345 kV since studies are more involved and lines more congested?
  Non-responsive INR’s moved to TBD status must pay fee to move forward from that status
  Reduced Screening Study scope options

## Slide 53: Possible Changes to Interconnection Process New reduction of Screening Study Scope
Screening Study Basic. This option consists of:
  appropriate case(s) will be used
  one POI will be studied
  no transmission projects to allow full output will be studied
  current fee schedule price
  completed in 90 business days
  Normal Tracking and Coordination
Effective will all screening studies submitted after 7/31
SS will only use generation meeting PG 6.9(1)
No loop stations will be created for study