## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Chad Mulholland, NRG
ROS
October 11th, 2018

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    4 FMEs in the month of August(Only 2 Reviewed at PDCWG)
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 09/12/18
  SCT DC Tie Directive 9 – MSSC Whitepaper and Ancillary Service Requirements
  Review 2019 Ancillary Service Methodology
  Review PDCWG Scope and Goals Changes
  Discuss VPWG and PDCWG Joint Meeting
  Regulation & Frequency Control Reports

## Slide 4: Meeting Minutes
Review PDCWG Scope and Goals-Changes
The PDCWG is responsible for coordinating with ERCOT, the Operations Working Group (OWG), and other ERCOT working groups as appropriate to identify and recommend measures to support the Protocols, Operating Guides, Other Binding Documents, NERC Reliability Standards and performance criteria. The PDCWG will also investigate and recommend solutions to frequency control problems including those that may lead to stability issues that should be analyzed with DWG.
Provide feedback to DWG when there may be gaps in generator modeling for stability issues.
Perform analysis for system events that are determined by ERCOT to be a Frequency Measurable Event(FME) or as deemed necessary by the PDCWG.of 450 MW or greater.
Perform analysis for system events of +/- 0.1 Hz or greater.

## Slide 5: Frequency Measurable Events Performance

## Slide 6: Frequency Measurable Events
There were 4 FMEs in August(only 2 Reviewed at PDCWG)
  8/13/2018 22:59:57
    Loss of 1198 MW
    Interconnection Frequency Response:
    9 of 56 Evaluated Generation Resources( 1 of 26 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    9 of 56 Evaluated Generation Resources ( 1of 26 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.
  8/16/2018 12:44:29
    Loss of 443 MW
    Interconnection Frequency Response:
    11 of 50 Evaluated Generation Resources (4 of 43 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    14 of 50 Evaluated Generation Resources (5 of 43 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Frequency Measurable Events
  8/31/2018 12:03:57-Not reviewed at PDCWG
    Loss of 527 MW
    Interconnection Frequency Response:
    19 of 59 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    15 of 59 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  8/31/2018 22:33:37-Not reviewed at PDCWG
    Loss of 646 MW
    Interconnection Frequency Response:
    9 of 54 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    8 of 54 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 8: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 906.99 MW/0.1Hz

## Slide 9: Frequency Control Report
August 2018

## Slide 10: CPS1 Performance

## Slide 11: RMS1 Performance of ERCOT Frequency

## Slide 12: Frequency Profile Analysis

## Slide 13: Time Error Corrections

## Slide 14: ERCOT Total Energy

## Slide 15: ERCOT Total Energy from Wind Generation

## Slide 16: ERCOT % Energy from Wind Generation

## Slide 17
Questions?