## Slide 1
Proposed 2019 Ancillary Service Methodology
Preliminary Quantities
Oct 11, 2018
ROS
ERCOT Staff

## Slide 2: Schedule for Stakeholder Discussion
September 12, 2018 – PDCWG (2019 AS Methodology)
September 20, 2018 – OWG
September 24, 2018 – QMWG
October 10, 2018 – WMS
  WMS endorsed 2019 A/S methodology without the 1375 MW floor on Non Spinning quantities during On-peak hours (HE 7 thru 22)
October 11, 2018 – ROS
October 25, 2018 – TAC (Cancelled)
November 29, 2018 – TAC
Dec 11, 2018 – BOD

## Slide 3: Scope of Discussion
ERCOT is not proposing any changes to the Ancillary Service (A/S) Methodology for 2019.
  The A/S quantities for 2019 contained in this presentation are based on the methodology that was approved in December 2017.
  These quantities reflect moving forward the historic data on which these are based, unless otherwise noted.
A redline version of the draft methodology and spreadsheets that contain the associated quantities for January through September of 2019 have been posted on the meeting page on ercot.com for today’s meeting.

## Slide 4
Divider Slide
Divider Slide (optional)
Regulation Service

## Slide 5: Regulation Service Methodology – 2019
The preliminary Regulation quantities for January 2019 thru July 2019 in subsequent slides have been computed using current methodology (2017 and 2018 five-minute net load variability) and updated Wind Adjustment tables.
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed Wind capacity.
  These tables have been updated for 2019.

## Slide 6: Wind Adjustment Monthly Average Comparison

## Slide 7: Hourly Avg. Regulation Comparison

## Slide 8
Divider Slide
Divider Slide (optional)
Responsive Reserve Service

## Slide 9: Responsive Service Methodology (RRS) - 2019
The preliminary RRS quantities for January 2019 thru Aug. 2019 in subsequent slides have been computed using 2017 and 2018 system inertia conditions and RRS table updated in 2017.
Note that 2018 Jan thru May RRS quantities in this slide deck are different from the posted quantities.
  RRS quantities were incrementally adjusted starting Feb 2018 and then changed again in Jun 2018 following NPRR 815 implementation.
  In order to aid comparison, in this slide deck, the RRS quantities for entire 2018 have been recomputed using a methodology that is consistent with the current methodology used for computing 2019 RRS quantities.

## Slide 10: RRS Table (Updated in 2017)
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.25:1 | 2.11:1 | 1.99:1 | 1.87:1 | 1.77:1 | 1.69:1 | 1.61:1 | 1.54:1 | 1.47:1 | 1.41:1 | 1.36:1 | 1.3:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5246 | 4916 | 4620 | 4361 | 4132 | 3927 | 3743 | 3576 | 3424 | 3285 | 3157 | 3040
*RRS (MW) | 3229 | 3162 | 3090 | 3039 | 2984 | 2920 | 2868 | 2815 | 2772 | 2726 | 2676 | 2643
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.26:1 | 1.22:1 | 1.17:1 | 1.14:1 | 1.1:1 | 1.07:1 | 1.04:1 | 1.01:1 | 1.00:1 | 1.00:1 | 1.00:1 | 1.00:1 | 1.00:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 2932 | 2831 | 2737 | 2650 | 2569 | 2492 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS (MW) | 2594 | 2550 | 2523 | 2477 | 2446 | 2408 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated with limit of 50% limit on LRs.
**Red font in table above identifies study scenario where RRS needed < 2300 MW. 2300 MW floor will be used in RRS requirement determination.
***Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest

## Slide 11: RRS Jan 2019

## Slide 12: RRS Mar 2019

## Slide 13: RRS Jun 2019
*.

## Slide 14: RRS Jul 2019

## Slide 15: RRS Aug 2019

## Slide 16: Hourly Avg. RRS Comparison

## Slide 17
Divider Slide
Divider Slide (optional)
Non-Spin Reserve Service

## Slide 18: Non Spinning Reserve Methodology (NSRS) - 2019
The preliminary NSRS quantities for January 2019 thru Aug. 2019 in subsequent slides have been computed using current methodology and updated Wind Over-Forecast Error Adjustment tables.

## Slide 19: Wind Over-Forecast Error Adjustment Table - 2019
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed Wind capacity.
  This table has been updated for 2019.
Average hourly increase in Wind Forecast error per 1000 MW increase in installed Wind capacity = 40 MW
Notes: Average Hourly increase in 2018 = 45 MW

## Slide 20: NSRS Jan 2019
*1375 MW Floor in On-peak hours (HE 7 thru 22)

## Slide 21: NSRS March 2019

## Slide 22: NSRS June 2019

## Slide 23: NSRS July 2019

## Slide 24: NSRS Aug 2019

## Slide 25: Hourly Avg. NSRS Comparison

## Slide 26
Divider Slide
Divider Slide (optional)
Discussion