## Slide 1
EXAMPLE - Proposal for Change to Ramp Rate Calculation in Resource Limit Calculator
QMWG
Sean Chang, P.E.
Market Analysis
Alex Giarratano
Operations Analysis
10/15/2018

## Slide 2: Background
Low Sustainable Limit
At 5/2/2018 WMS, ERCOT presented a situation where operators performed a manual high dispatch limit (HDL) override due to a resource getting expected generation above high sustained limit (HSL)
At 6/4/2018 QMWG, ERCOT gave a tutorial on how this can happen due to a combination of static ramp sharing and regulation deployment
ERCOT proposed a dynamic ramp rate calculation at the 6/4/2018 QMWG and is bringing back analysis today
ERCOT presented analysis on impacts of dynamic ramp rate calculation at 9/24/2018 QMWG

## Slide 3: Terms and Definitions
Low Sustainable Limit
HSL
LSL
Telemetered Values
High Sustainable Limit (HSL)
Low Sustainable Limit (LSL)
Power Output (MW)
Normal Up Ramp Rate
Normal Down Ramp Rate
Calculated Values
High Ancillary Service Limit (HASL)
Low Ancillary Service Limit (LASL)
SCED Up Ramp Rate
SCED Down Ramp Rate
High Dispatch Limit (HDL)
Low Dispatch Limit (LDL)
Output Values
Base Point (BP)
HASL
LASL
MW
BP
HDL
LDL
This slide is the same as the tutorial from the 6/4/2018 QMWG slide deck

## Slide 4: Current: 30 MW REGUP, 450 MW SCED BP
450
Input Values | MW
High Sustainable Limit (HSL) | 500
Power Output (MW) | 480
Normal Up Ramp Rate | 50
Normal Down Ramp Rate | 50
REG UP Responsibility | 50
REG DN Responsibility | 50
Calculated Values | MW
High Ancillary Service Limit (HASL) | 450
SCED Up Ramp Rate | 15
SCED Down Ramp Rate | 15
High Dispatch Limit (HDL) | 465
Low Dispatch Limit (LDL) | 465
Output Values | MW
Possible Base Point (BP) | 465
500
480
465
465
If over 35 MW of regulation up is deployed in the next 5 minutes, expected generation > HSL
Resource’s HDL gets locked to LDL because it’s ramp rate can’t take it back below HASL

## Slide 5: Proposed Methodology with Reg. Up. Example
Low Sustainable Limit
Current
SCED Down Ramp Rate =
= Normal Down Ramp Rate – Regulation Down Responsibility / 7
SCED Down Ramp Rate = 10 – 50 / 7 = 2.86 MW/min
Proposed
SCED Down Ramp Rate =
= Normal Down Ramp Rate
– [ (1 – Percentage of Up Regulation Deployed )
* Regulation Down Responsibility / 7 ]
SCED Down Ramp Rate = 10 – [ (1 – 0.6) * 50 / 7 ] = 7.14 MW/min
See 9/24/2018 QMWG presentation for full proposed methodology and example: http://www.ercot.com/calendar/2018/9/24/162077-QMWG

## Slide 6: Proposed: 30 MW REGUP, 450 MW SCED BP
450
Input Values | MW
High Sustainable Limit (HSL) | 500
Power Output (MW) | 480
Normal Up Ramp Rate | 50
Normal Down Ramp Rate | 50
REG UP Responsibility | 50
REG DN Responsibility | 50
Calculated Values | MW
High Ancillary Service Limit (HASL) | 450
SCED Up Ramp Rate | 15
SCED Down Ramp Rate | 35
High Dispatch Limit (HDL) | 450
Low Dispatch Limit (LDL) | 445
Output Values | MW
Possible Base Point (BP) | 445–450
500
480
445
From 9/24/2018 QMWG analysis, it is unlikely for regulation down to be fully deployed