## Slide 1
ERCOT Frequency Control Report
July 2018
ERCOT
Operations Planning
PDCWG | October 22nd, 2018

## Slide 2: Summary of September 2018
CPS1: 174.40%
Current CPS1 12-Month Rolling Average: 176.01%
7 BAAL Exceedances
  Loss of ICCP Event
  Unit Losses
2 hourly CPS1 scores below 100%
BAAL-003 Events have not been updated past May
2018 BAAL-003 FRM Performance: -788.77
2018 RMS1 Statistics
  Mean: 15.15 mHz
  Min: 13.77 mHz
  Max: 17.84 mHz
September Energy Statistics
  Total Energy: 32,513,579 MWh
  Wind Energy: 3,770,566 MWh
  Percent Energy from Wind Generation: 11.60%
September Minimum System Inertia
  Mean: 251,051
  Min: 196,700 on September 30th
  Max: 281,526 on September 6th
Notes: Wind Energy lower than 2017

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
September-18 CPS1 (%): 174.40
Notes: Outliers:
9/11/18 16:00: 100.87%
Large expected generation deviation. Regulation exhausted from 4:15 PM until 4:27 PM.
9/23/18 16:00: 68.75%
ICCP Event. Units ramped down by approximately 950 MW. Regulation exhausted several times throughout the hour.
9/26/18 13:00: 89.16%
Wind dropped by approximately 2,257 MW throughout the hour. Regulation exhausted from 13:10 until 13:17. Loss of 1006 MW at 13:54.

## Slide 5: BAAL Exceedances & Violations
There were 7 BAAL exceedances
  September 23, 2018
    Loss of ICCP Event
    950 MW of generation ramp down
    Less than 59.91 Hz for 3 minutes
  September 26, 2018
    Unit trip at 13:54:03
    Loss of 1006 MW
    Less than 59.91 Hz for 3 minutes
  September 28, 2018
    Unit trip at 12:00:14
    Loss of 837 MW
    Less than 59.91 Hz for 1 minute

## Slide 6: 15-Minute Average CPS1%
September-18 CPS1 (%): 174.40

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 176.01%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 14.69 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 15.15 mHz
Min: 13.77 mHz
Max: 17.84 mHz

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Frequency Profile Comparison

## Slide 15: Time Error Correction

## Slide 16: ERCOT Daily Time Error

## Slide 17: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 18: BAL-003 Performance

## Slide 19: Op. Year 2018 BAL-003 Selected Events
 | BA |  | BA | BA | Value "A" Information (MW) |  | Value "B" Information (MW) |  | SEFRD (FRM) |  | Exclude
Date/Time (t-0) | Time | B to A |  | Bias |  |  |  |  | for Bias | for R1 | for data
BA Time | Zone | DelFreq | Time | DelFreq | Load Loss | Adjust | Load Loss | Adjust. | (MW/0.1Hz) | (MW/0.1Hz) | error *
2/5/2018 14:04:41 | CST | -0.098 | 14:04:46 | -0.098 | 0.0 | 0.0 | 816.0 | 0.0 | -829.9 | -829.9 | N
2/14/2018 06:30:17 | CST | -0.105 | 6:30:21 | -0.105 | 0.0 | 0.0 | 784.2 | 0.0 | -747.7 | -747.7 | N
3/5/2018 00:51:20 | CST | -0.033 | 6:51:20 | -0.033 | 0.0 | 0.0 | 513.5 | 0.0 | -1552.2 | -1552.2 | N
3/24/2018 15:47:15 | CDT | -0.085 | 20:47:15 | -0.085 | 0.0 | 0.0 | 797.3 | 0.0 | -943.3 | -943.3 | N
3/29/2018 10:09:40 | CDT | -0.041 | 16:09:40 | -0.041 | 0.0 | 0.0 | 434.1 | 0.0 | -1049.1 | -1049.1 | N
4/13/2018 20:02:08 | CDT | -0.076 | 2:02:08 | -0.076 | 0.0 | 0.0 | 438.0 | 0.0 | -577.9 | -577.9 | N
4/14/2018 19:11:25 | CDT | -0.048 | 1:11:25 | -0.048 | 0.0 | 0.0 | 349.0 | 0.0 |  |  | Y
4/28/2018 12:15:43 | CDT | -0.048 | 18:15:43 | -0.048 | 0.0 | 0.0 | 408.0 | 0.0 |  |  | Y
5/5/2018 10:19:04 | CDT | -0.095 | 16:19:04 | -0.095 | 0.0 | 0.0 | 536.3 | 0.0 | -563.5 | -563.5 | N
5/21/2018 02:06:23 | CDT | -0.081 | 8:06:23 | -0.081 | 0.0 | 0.0 | 460.5 | 0.0 | -568.4 | -568.4 | N
Maybe. Will be valuated at the end of the year.

## Slide 20: Op. Year 2018 BAL-003 FRM Performance
FRM Performance Results for 2018 | 
2018 | Current data year (December thru November)
-381.0 | Operating Year 2019 BA Frequency Response Obligation (FRO) for next year's FRM
-381.0 | Operating Year 2018 BA Frequency Response Obligation (FRO)
-788.77 | 2018 FRM - Median Estimated Frequency Response MW/0.1Hz for BA Compliance to R1, minimum Frequency Response
-854.0 | 2018 FRM - Average Estimated Frequency Response MW/0.1 Hz using SEFRD for R1
0.0 | 2018 FRM - Regression Estimated Frequency Response MW/0.1Hz using SEFRD for R1

## Slide 21: ERCOT Energy Statistics

## Slide 22: Total Energy
Notes: 32,513,579 MWh

## Slide 23: Total Energy from Wind Generation
Notes: 3,770,566 MWh

## Slide 24: % Energy from Wind Generation
Notes: 11.60%

## Slide 25: ERCOT System Inertia

## Slide 26: Daily Minimum System Inertia
Notes: Minimum Inertia = 130,014 MW*s on 10/27/2017. This was also our record wind day.
September
Mean: 251,051
Max: 281,526 on September 6th
Min: 196,700 on September 30th

## Slide 27: Questions?
Thank you!

## Slide 28: Op. Year 2017 BAL-003 Selected Events
Notes: Frequency Bias updated from 764 to 759 in April

## Slide 29: Op. Year 2017 BAL-003 FRM Performance