## BranchViol
Monitored Facility | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Cont ID | Base Flow (MVA) | Cont Flow (MVA) | Final DC %Loading | Final AC %Loading | Severity Rank | Radial Index | Base MW Flow | Cont MW Flow | Base MVAR Flow | Cont MVAR Flow | Fr Base Volt | Fr Cont Volt | To Base Volt | To Cont Volt | Base dAngle [deg] | Cont dAngle [deg]
902 POES31569 69.0 981 SPNCRINT69 69.0 1 | 902 | POES31569 | 981 | SPNCRINT69 | 1 | 69 | 19 | 115 | 115 | Base Case | 0 | 117.7 | - | 102.32 | 102.35 | 0 | 1 | 117.7 | - | -3 | - | 1 | - | 1.0034 | - | 5.61 | -
981 SPNCRINT69 69.0 982 DN_STEAM_8 138 1 | 981 | SPNCRINT69 | 982 | DN_STEAM_8 | 1 | 69/138 | 19/12 | 125 | 130 | Base Case | 0 | 119.7 | - | 93.77 | 95.72 | 0 | 1 | 117.2 | - | -14.5 | - | 1.0034 | - | 1.0102 | - | 5.59 | -
1624 LEONSW_8 138 6310 PUTN4B 138 1 | 1624 | LEONSW_8 | 6310 | PUTN4B | 1 | 138 | 1/6 | 72 | 84 | Base Case | 0 | 68.1 | - | 78.58 | 94.62 | 0 | 0.65874 | 56.6 | - | -39 | - | 1.0088 | - | 1.0211 | - | 6.64 | -
8825 SURRCFE4 138 86107 CUF-138 138 1 | 8825 | SURRCFE4 | 86107 | CUF-138 | 1 | 138 | 18/24 | 329 | 329 | Base Case | 0 | 301 | - | 90.85 | 91.49 | 0 | 1 | -298.9 | - | 12 | - | 0.9938 | - | 1.01 | - | 6.76 | -
110127 DOWGEN_2_8 138 110128 DOWGEN_3_8 138 SG | 110127 | DOWGEN_2_8 | 110128 | DOWGEN_3_8 | SG | 138 | 904 | 120 | 120 | Base Case | 0 | 109 | - | 85.06 | 90.83 | 0 | 1 | 102.1 | - | 26.1 | - | 0.9667 | - | 0.9665 | - | 0.02 | -
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 821 FIREWHEEL 138 833 WYLIESW 138 1 | 614 | 193.6 | 271.6 | 123.86 | 124.6 | 1 | 0.814 | 194.1 | 271 | 14 | 21.7 | 1.0055 | 1.0011 | 0.999 | 0.9919 | 1.6 | 2.25
802 APOLLO 138 825 NAAMAN 138 1 | 802 | APOLLO | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 821 FIREWHEEL 138 833 WYLIESW 138 1 | 614 | 170.8 | 248.6 | 112.97 | 114.05 | 1 | 0.72553 | -169.5 | -244.2 | 1.2 | 5.8 | 0.9923 | 0.9825 | 0.999 | 0.9919 | 2.11 | 3.11
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 821 FIREWHEEL 138 835 HOLFORD 138 1 | 615 | 193.6 | 258.7 | 118.19 | 118.65 | 2 | 0.814 | 194.1 | 258.7 | 14 | 17.5 | 1.0055 | 1.0023 | 0.999 | 0.994 | 1.6 | 2.15
802 APOLLO 138 825 NAAMAN 138 1 | 802 | APOLLO | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 821 FIREWHEEL 138 835 HOLFORD 138 1 | 615 | 170.8 | 235.8 | 107.3 | 108.15 | 2 | 0.72553 | -169.5 | -232.3 | 1.2 | 7.7 | 0.9923 | 0.9857 | 0.999 | 0.994 | 2.11 | 2.95
805 FAIRDALE 138 823 WALNUT 138 1 | 805 | FAIRDALE | 823 | WALNUT | 1 | 138 | 20 | 218 | 218 | 823 WALNUT 138 849 NEWMAN8 138 1 | 618 | 144.9 | 201.4 | 92.67 | 92.41 | 2 | 0.91593 | 145.8 | 201.9 | 6.3 | 16.8 | 1.0075 | 1.0059 | 1.0055 | 1.0026 | 0.54 | 0.74
805 FAIRDALE 138 823 WALNUT 138 1 | 805 | FAIRDALE | 823 | WALNUT | 1 | 138 | 20 | 218 | 218 | 824 MILLER 138 849 NEWMAN8 138 1 | 619 | 144.9 | 212.7 | 98.26 | 97.57 | 1 | 0.91593 | 145.8 | 214.2 | 6.3 | -0.5 | 1.0075 | 1.0069 | 1.0055 | 1.0047 | 0.54 | 0.79
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 828 LOOKOUT 138 835 HOLFORD 138 1 | 622 | 193.6 | 235.9 | 108.09 | 108.21 | 3 | 0.814 | 194.1 | 236.7 | 14 | 10.4 | 1.0055 | 1.0044 | 0.999 | 0.9975 | 1.6 | 1.96
802 APOLLO 138 825 NAAMAN 138 1 | 802 | APOLLO | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 828 LOOKOUT 138 835 HOLFORD 138 1 | 622 | 170.8 | 213.2 | 97.2 | 97.79 | 3 | 0.72553 | -169.5 | -211 | 1.2 | 10.9 | 0.9923 | 0.991 | 0.999 | 0.9975 | 2.11 | 2.66
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 968 BENDAVIS_8 138 2477 PRKMXCRK1_8 138 1 | 707 | 193.6 | 212.7 | 97.31 | 97.59 | 4 | 0.79869 | 194.1 | 213.4 | 14 | 15.5 | 1.0055 | 1.0058 | 0.999 | 0.9987 | 1.6 | 1.76
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 968 BENDAVIS_8 138 2696 MURPHY1_8 138 1 | 708 | 193.6 | 206.2 | 94.29 | 94.6 | 5 | 0.79639 | 194.1 | 206.9 | 14 | 15.9 | 1.0055 | 1.0062 | 0.999 | 0.9992 | 1.6 | 1.7
6666 ALPINE2A 69.0 6674 BRONCO2A 69.0 1 | 6666 | ALPINE2A | 6674 | BRONCO2A | 1 | 69 | 6 | 48 | 53 | 1009 YUCCADR_8 138 11245 WARD1927_8 138 1 | 729 | 42.2 | 49.6 | 85.35 | 93.55 | 1 | 0.83133 | -37.1 | -44.3 | 21.3 | 23 | 1.0181 | 1.0107 | 1.0095 | 1.0082 | 6.71 | 7.94
37921 TNWINKTP__0 69.0 37940 TNCALIFRNA0 69.0 1 | 37921 | TNWINKTP__0 | 37940 | TNCALIFRNA0 | 1 | 69 | 1200/17 | 63 | 63 | 1013 WOLFSS_8 138 37981 TNWICKETT_1 138 1 | 742 | 0.5 | 58.1 | 92.59 | 92.15 | 1 | 0.94862 | -0.5 | 54.8 | -0.1 | -18.3 | 0.9956 | 0.9962 | 0.9957 | 0.9946 | 0.01 | 1.17
37940 TNCALIFRNA0 69.0 37960 TNWNKLRCO60 69.0 1 | 37940 | TNCALIFRNA0 | 37960 | TNWNKLRCO60 | 1 | 69 | 17 | 62 | 62 | 1013 WOLFSS_8 138 37981 TNWICKETT_1 138 1 | 742 | 3.3 | 55.9 | 89.9 | 90.15 | 1 | 0.79603 | -3.1 | 51.8 | -0.9 | -20.2 | 0.9957 | 0.9946 | 0.9985 | 0.9931 | 0.2 | 4.51
1234 PGASUSTA_9 69.0 1276 PLESNTFARM_9 69.0 1 | 1234 | PGASUSTA_9 | 1276 | PLESNTFARM_9 | 1 | 69 | 1 | 42 | 42 | 1196 CRANE_8 138 76615 L_LCRANE8_1Y 138 1 | 975 | 2.1 | 39.9 | 78.55 | 94.95 | 1 | 1 | -0.8 | 34.4 | 1.9 | 9.9 | 0.9902 | 0.8985 | 0.989 | 0.8657 | 0.11 | 1.86
1123 ODESSANO_9 69.0 1234 PGASUSTA_9 69.0 1 | 1123 | ODESSANO_9 | 1234 | PGASUSTA_9 | 1 | 69 | 1 | 42 | 42 | 1196 CRANE_8 138 76615 L_LCRANE8_1Y 138 1 | 975 | 2 | 39.8 | 78.57 | 94.88 | 1 | 1 | -0.8 | 36.8 | 1.5 | 13.3 | 0.993 | 0.9856 | 0.9902 | 0.8985 | 0.26 | 4.19
1957 SAGINAW1_8 138 2043 WATAGAN_T8 138 1 | 1957 | SAGINAW1_8 | 2043 | WATAGAN_T8 | 1 | 138 | 1 | 614 | 614 | 1852 ROANOKE2_8 138 15100 PARKVISTA1_8 138 1 | 1641 | 244.3 | 663.9 | 86.61 | 108.12 | 1 | 1 | 240.5 | 545.8 | 52.2 | 362 | 1.008 | 0.987 | 0.9939 | 0.9088 | 2.68 | 6.49
2039 MEADPRK1_8 138 2043 WATAGAN_T8 138 1 | 2039 | MEADPRK1_8 | 2043 | WATAGAN_T8 | 1 | 138 | 1 | 614 | 614 | 1852 ROANOKE2_8 138 15100 PARKVISTA1_8 138 1 | 1641 | 217.3 | 634.8 | 82.16 | 103.39 | 1 | 1 | -213.2 | -509.8 | -32.5 | -256.1 | 0.9923 | 0.8988 | 0.9939 | 0.9088 | 0.35 | 0.98
2039 MEADPRK1_8 138 2042 SMITHFD2_8 138 1 | 2039 | MEADPRK1_8 | 2042 | SMITHFD2_8 | 1 | 138 | 1 | 614 | 614 | 1852 ROANOKE2_8 138 15100 PARKVISTA1_8 138 1 | 1641 | 187 | 601.6 | 77.4 | 97.98 | 1 | 1 | 184 | 480.6 | 23.9 | 247.5 | 0.9923 | 0.8988 | 0.9888 | 0.8713 | 0.92 | 2.9
1852 ROANOKE2_8 138 15100 PARKVISTA1_8 138 1 | 1852 | ROANOKE2_8 | 15100 | PARKVISTA1_8 | 1 | 138 | 1 | 502 | 502 | 1957 SAGINAW1_8 138 2043 WATAGAN_T8 138 1 | 1786 | 318.4 | 581 | 105.93 | 115.73 | 1 | 1 | 292.3 | 536.7 | 134.7 | 225.6 | 1.0117 | 1.0024 | 0.9961 | 0.9763 | 1.53 | 2.92
2058 CIRCLET_P8 138 15100 PARKVISTA1_8 138 1 | 2058 | CIRCLET_P8 | 15100 | PARKVISTA1_8 | 1 | 138 | 1 | 478 | 478 | 1957 SAGINAW1_8 138 2043 WATAGAN_T8 138 1 | 1786 | 225.9 | 487.2 | 94.02 | 101.92 | 1 | 1 | -208.8 | -450.2 | -82.3 | -145.7 | 0.9935 | 0.9713 | 0.9961 | 0.9763 | 0.29 | 0.65
2036 KELLER2_T8 138 2058 CIRCLET_P8 138 1 | 2036 | KELLER2_T8 | 2058 | CIRCLET_P8 | 1 | 138 | 1 | 478 | 478 | 1957 SAGINAW1_8 138 2043 WATAGAN_T8 138 1 | 1786 | 207 | 467.7 | 90.22 | 97.85 | 1 | 1 | -190.5 | -431 | -74.7 | -129.6 | 0.9889 | 0.9623 | 0.9935 | 0.9713 | 0.51 | 1.23
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 1978 MCKNYN1_8 138 2341 TRINITYFL_T8 138 1 | 1821 | 193.6 | 207.1 | 94.31 | 95.01 | 2 | 0.79602 | 194.1 | 207 | 14 | 18 | 1.0055 | 1.0034 | 0.999 | 0.996 | 1.6 | 1.71
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 1979 MCKNYN2_8 138 2544 CHAMBVLE_P8 138 1 | 1823 | 193.6 | 206.8 | 94.23 | 94.84 | 5 | 0.79602 | 194.1 | 206.8 | 14 | 17 | 1.0055 | 1.0037 | 0.999 | 0.9965 | 1.6 | 1.71
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 1979 MCKNYN2_8 138 2546 MCKNY2_8 138 1 | 1824 | 193.6 | 206.8 | 94.23 | 94.84 | 4 | 0.79602 | 194.1 | 206.8 | 14 | 17 | 1.0055 | 1.0037 | 0.999 | 0.9965 | 1.6 | 1.71
1852 ROANOKE2_8 138 15100 PARKVISTA1_8 138 1 | 1852 | ROANOKE2_8 | 15100 | PARKVISTA1_8 | 1 | 138 | 1 | 502 | 502 | 2039 MEADPRK1_8 138 2042 SMITHFD2_8 138 1 | 1881 | 318.4 | 512.4 | 94.67 | 102.08 | 3 | 1 | 292.3 | 479.3 | 134.7 | 189 | 1.0117 | 1.0059 | 0.9961 | 0.9837 | 1.53 | 2.58
1852 ROANOKE2_8 138 15100 PARKVISTA1_8 138 1 | 1852 | ROANOKE2_8 | 15100 | PARKVISTA1_8 | 1 | 138 | 1 | 502 | 502 | 2039 MEADPRK1_8 138 2043 WATAGAN_T8 138 1 | 1882 | 318.4 | 548.3 | 100.49 | 109.21 | 2 | 1 | 292.3 | 509.6 | 134.7 | 207.7 | 1.0117 | 1.0041 | 0.9961 | 0.9799 | 1.53 | 2.76
2058 CIRCLET_P8 138 15100 PARKVISTA1_8 138 1 | 2058 | CIRCLET_P8 | 15100 | PARKVISTA1_8 | 1 | 138 | 1 | 478 | 478 | 2039 MEADPRK1_8 138 2043 WATAGAN_T8 138 1 | 1882 | 225.9 | 454.9 | 88.31 | 95.18 | 2 | 1 | -208.8 | -423.6 | -82.3 | -132.1 | 0.9935 | 0.9754 | 0.9961 | 0.9799 | 0.29 | 0.61
2036 KELLER2_T8 138 2058 CIRCLET_P8 138 1 | 2036 | KELLER2_T8 | 2058 | CIRCLET_P8 | 1 | 138 | 1 | 478 | 478 | 2039 MEADPRK1_8 138 2043 WATAGAN_T8 138 1 | 1882 | 207 | 435.6 | 84.5 | 91.12 | 2 | 1 | -190.5 | -404.6 | -74.7 | -117.5 | 0.9889 | 0.9672 | 0.9935 | 0.9754 | 0.51 | 1.14
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2341 TRINITYFL_T8 138 2374 ANNASW_8 138 1 | 2071 | 193.6 | 207.1 | 94.31 | 95 | 3 | 0.79602 | 194.1 | 207 | 14 | 17.9 | 1.0055 | 1.0034 | 0.999 | 0.996 | 1.6 | 1.71
659 BRIDGES 138 2518 COLONY_8 138 1 | 659 | BRIDGES | 2518 | COLONY_8 | 1 | 138 | 11/1 | 326 | 326 | 2370 COLLINSS1_8 138 33629 ROMANJUAREZ2 138 1 | 2128 | 62.8 | 295.3 | 88.32 | 90.6 | 1 | 1 | -30.4 | -282.8 | -55.2 | -64.2 | 1.0036 | 0.9819 | 1.0074 | 0.9876 | 0.1 | 1.11
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2374 ANNASW_8 138 2544 CHAMBVLE_P8 138 1 | 2131 | 193.6 | 207.8 | 94.68 | 95.34 | 1 | 0.79602 | 194.1 | 207.8 | 14 | 17.5 | 1.0055 | 1.0035 | 0.999 | 0.9962 | 1.6 | 1.71
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2469 ROYSES_A8 138 12702 FATE1_8 138 1 | 2310 | 193.6 | 249.7 | 113.79 | 114.54 | 1 | 0.80142 | 194.1 | 249 | 14 | 24.2 | 1.0055 | 1.0021 | 0.999 | 0.9929 | 1.6 | 2.06
802 APOLLO 138 825 NAAMAN 138 1 | 802 | APOLLO | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2469 ROYSES_A8 138 12702 FATE1_8 138 1 | 2310 | 170.8 | 226.7 | 102.9 | 103.98 | 1 | 0.70698 | -169.5 | -222.9 | 1.2 | -0.7 | 0.9923 | 0.9833 | 0.999 | 0.9929 | 2.11 | 2.82
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2700 GARLW1_8 138 2701 GARL1_8 138 1 | 2504 | 193.6 | 228.1 | 104.37 | 104.63 | 5 | 0.80142 | 194.1 | 228.6 | 14 | 14.3 | 1.0055 | 1.0044 | 0.999 | 0.9971 | 1.6 | 1.89
802 APOLLO 138 825 NAAMAN 138 1 | 802 | APOLLO | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2700 GARLW1_8 138 2701 GARL1_8 138 1 | 2504 | 170.8 | 205.3 | 93.48 | 94.16 | 5 | 0.70698 | -169.5 | -203.1 | 1.2 | 5.7 | 0.9923 | 0.9898 | 0.999 | 0.9971 | 2.11 | 2.55
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2701 GARL1_8 138 12736 ROWLETT_T8 138 1 | 2506 | 193.6 | 233.8 | 106.86 | 107.25 | 3 | 0.80142 | 194.1 | 234.1 | 14 | 16.8 | 1.0055 | 1.0038 | 0.999 | 0.9961 | 1.6 | 1.93
802 APOLLO 138 825 NAAMAN 138 1 | 802 | APOLLO | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2701 GARL1_8 138 12736 ROWLETT_T8 138 1 | 2506 | 170.8 | 210.9 | 95.97 | 96.76 | 3 | 0.70698 | -169.5 | -208.4 | 1.2 | 4.2 | 0.9923 | 0.9882 | 0.999 | 0.9961 | 2.11 | 2.62
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2702 RCKWL_8 138 12702 FATE1_8 138 1 | 2507 | 193.6 | 245.4 | 111.94 | 112.55 | 2 | 0.80142 | 194.1 | 245 | 14 | 22.2 | 1.0055 | 1.0026 | 0.999 | 0.9938 | 1.6 | 2.03
802 APOLLO 138 825 NAAMAN 138 1 | 802 | APOLLO | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2702 RCKWL_8 138 12702 FATE1_8 138 1 | 2507 | 170.8 | 222.4 | 101.05 | 102.01 | 2 | 0.70698 | -169.5 | -219 | 1.2 | 0.6 | 0.9923 | 0.9846 | 0.999 | 0.9938 | 2.11 | 2.77
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2702 RCKWL_8 138 12734 CHIESA2_8 138 1 | 2508 | 193.6 | 233.8 | 106.98 | 107.24 | 4 | 0.80142 | 194.1 | 234.1 | 14 | 16.6 | 1.0055 | 1.0038 | 0.999 | 0.9961 | 1.6 | 1.93
802 APOLLO 138 825 NAAMAN 138 1 | 802 | APOLLO | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2702 RCKWL_8 138 12734 CHIESA2_8 138 1 | 2508 | 170.8 | 210.9 | 96.09 | 96.75 | 4 | 0.70698 | -169.5 | -208.4 | 1.2 | 4.4 | 0.9923 | 0.9883 | 0.999 | 0.9961 | 2.11 | 2.62
196 FAIRFIELD 138 3505 BIGBRN_T_8 138 1 | 196 | FAIRFIELD | 3505 | BIGBRN_T_8 | 1 | 138 | 11/1 | 84 | 84 | 3394 JEWETTA_8 138 3501 SEATEAG_T_8 138 1 | 3030 | 28.6 | 79 | 92.45 | 93.99 | 1 | 1 | -28.7 | -78.2 | -2.6 | -4.5 | 1.0061 | 0.9915 | 1.0086 | 0.9981 | 0.18 | 0.53
3400 TWIN_OAK_N5 345 120135 OAKGROV2_5 345 1 | 3400 | TWIN_OAK_N5 | 120135 | OAKGROV2_5 | 1 | 345 | 1/901 | 1631 | 1631 | 3400 TWIN_OAK_N5 345 120134 OAKGROV1_5 345 1 | 3039 | 783.6 | 1616.5 | 101.82 | 99.11 | 1 | 1 | -804.1 | -1659.4 | -104.9 | -210.9 | 1.0348 | 1.0348 | 1.0367 | 1.0387 | 0.45 | 0.94
3400 TWIN_OAK_N5 345 120134 OAKGROV1_5 345 1 | 3400 | TWIN_OAK_N5 | 120134 | OAKGROV1_5 | 1 | 345 | 1/901 | 1631 | 1631 | 3400 TWIN_OAK_N5 345 120135 OAKGROV2_5 345 1 | 3040 | 834.2 | 1616.5 | 101.82 | 99.11 | 1 | 1 | -856.7 | -1659.4 | -106 | -210.9 | 1.0348 | 1.0348 | 1.0367 | 1.0386 | 0.45 | 0.87
3410 LAKE_CRK1_8 138 3452 WACOLASA1_8 138 1 | 3410 | LAKE_CRK1_8 | 3452 | WACOLASA1_8 | 1 | 138 | 1 | 372 | 372 | 3407 ELM_MOTT__8 138 3575 NCRTP_T_8 138 1 | 3047 | 221.3 | 349.6 | 94.72 | 93.98 | 1 | 0.82578 | 226.3 | 355.5 | -12.7 | 21.6 | 1.0239 | 1.0188 | 1.0206 | 1.0064 | 2.43 | 3.82
3438 WACO_E1_8 138 3452 WACOLASA1_8 138 1 | 3438 | WACO_E1_8 | 3452 | WACOLASA1_8 | 1 | 138 | 1 | 372 | 372 | 3407 ELM_MOTT__8 138 3575 NCRTP_T_8 138 1 | 3047 | 218.8 | 347 | 93.44 | 93.28 | 1 | 0.91155 | -221.5 | -347.4 | 25.7 | 12.8 | 1.0196 | 1.0019 | 1.0206 | 1.0064 | 1.22 | 1.96
3479 NAVARRO1_9 69.0 3486 RICHLAND1_9 69.0 1 | 3479 | NAVARRO1_9 | 3486 | RICHLAND1_9 | 1 | 69 | 1 | 36 | 36 | 3597 GROESBECP_8 138 3634 GROES_SE1_8 138 1 | 3181 | 17.2 | 55.5 | 142.69 | 154.14 | 1 | 1 | 17.2 | 49.6 | -0.2 | 22.5 | 0.9961 | 0.983 | 0.9822 | 0.9154 | 1.19 | 2.53
3486 RICHLAND1_9 69.0 3487 WRTHMPOD_9 69.0 1 | 3486 | RICHLAND1_9 | 3487 | WRTHMPOD_9 | 1 | 69 | 1 | 36 | 36 | 3597 GROESBECP_8 138 3634 GROES_SE1_8 138 1 | 3181 | 15.3 | 53.4 | 136.62 | 148.33 | 1 | 1 | 15 | 45.2 | -0.8 | 18.6 | 0.9822 | 0.9154 | 0.9707 | 0.8564 | 0.91 | 2.09
3487 WRTHMPOD_9 69.0 3605 WORTHAM1_9 69.0 1 | 3487 | WRTHMPOD_9 | 3605 | WORTHAM1_9 | 1 | 69 | 1 | 36 | 36 | 3597 GROESBECP_8 138 3634 GROES_SE1_8 138 1 | 3181 | 4.4 | 39.3 | 102.62 | 109.04 | 1 | 1 | 2.7 | 30.7 | -3.3 | 13.5 | 0.9707 | 0.8564 | 0.9722 | 0.8097 | 0.35 | 1.99
3605 WORTHAM1_9 69.0 3606 MEXIA2_T_9 69.0 1 | 3605 | WORTHAM1_9 | 3606 | MEXIA2_T_9 | 1 | 69 | 1 | 37 | 37 | 3597 GROESBECP_8 138 3634 GROES_SE1_8 138 1 | 3181 | 3.7 | 36.9 | 94.47 | 99.71 | 1 | 1 | 0.8 | 27.6 | -3.5 | 11.5 | 0.9722 | 0.8097 | 0.9749 | 0.7748 | 0.18 | 1.56
3479 NAVARRO1_9 69.0 3486 RICHLAND1_9 69.0 1 | 3479 | NAVARRO1_9 | 3486 | RICHLAND1_9 | 1 | 69 | 1 | 36 | 36 | 3632 MEXIA2_1_8 138 3634 GROES_SE1_8 138 1 | 3216 | 17.2 | 46 | 111.44 | 127.67 | 2 | 1 | 17.2 | 42.1 | -0.2 | 15.9 | 0.9961 | 0.9802 | 0.9822 | 0.9265 | 1.19 | 2.29
3486 RICHLAND1_9 69.0 3487 WRTHMPOD_9 69.0 1 | 3486 | RICHLAND1_9 | 3487 | WRTHMPOD_9 | 1 | 69 | 1 | 36 | 36 | 3632 MEXIA2_1_8 138 3634 GROES_SE1_8 138 1 | 3216 | 15.3 | 43.9 | 105.37 | 121.82 | 2 | 1 | 15 | 38.4 | -0.8 | 13.1 | 0.9822 | 0.9265 | 0.9707 | 0.8797 | 0.91 | 1.86
5715 TORDILLOSW9 69.0 5721 MCCOYSUB9 69.0 1 | 5715 | TORDILLOSW9 | 5721 | MCCOYSUB9 | 1 | 69 | 13 | 40 | 45 | 5390 SOMERSET 138 5718 ROSSVILLESB8 138 1 | 3451 | 26.7 | 43.6 | 91.36 | 96.89 | 1 | 0.8933 | 25.7 | 43.8 | -8.8 | -1.4 | 1.0194 | 1.0054 | 1.0088 | 0.9696 | 2.31 | 3.44
5714 PLEASANTNSB9 69.0 5721 MCCOYSUB9 69.0 1 | 5714 | PLEASANTNSB9 | 5721 | MCCOYSUB9 | 1 | 69 | 13 | 40 | 45 | 5390 SOMERSET 138 5718 ROSSVILLESB8 138 1 | 3451 | 25.8 | 42.7 | 87.5 | 94.83 | 1 | 0.85265 | -23.3 | -38.9 | 10.7 | 6.9 | 0.9979 | 0.9274 | 1.0088 | 0.9696 | 3.17 | 5.05
5500 RAYBURN9 69.0 5502 RAYBURN8 138 1 | 5500 | RAYBURN9 | 5502 | RAYBURN8 | 1 | 69/138 | 13 | 84 | 84 | 5502 RAYBURN8 138 5584 VANDERBLTSW8 138 1 | 3477 | 54.1 | 75.9 | 90.05 | 90.32 | 1 | 0.52158 | -53.9 | -75.4 | 4.8 | 8.1 | 1.014 | 1.014 | 1.014 | 1.014 | 5.3 | 7.44
8119 BLESSING2A 69.0 8550 MARKHAM2A 69.0 1 | 8119 | BLESSING2A | 8550 | MARKHAM2A | 1 | 69 | 8 | 61 | 61 | 5544 DANEVANGSW9 69.0 5548 DANEVANGSUB9 69.0 1 | 3504 | 36.7 | 66.7 | 105.57 | 109.32 | 1 | 0.84557 | 36.8 | 65.8 | -4.6 | 6.3 | 1.0104 | 0.9922 | 0.997 | 0.9481 | 3.21 | 5.64
5554 MARKHAMTAP9 69.0 5555 SHROPSHRSUB9 69.0 1 | 5554 | MARKHAMTAP9 | 5555 | SHROPSHRSUB9 | 1 | 69 | 13 | 40 | 45 | 5544 DANEVANGSW9 69.0 5548 DANEVANGSUB9 69.0 1 | 3504 | 5.1 | 48.1 | 98.02 | 106.82 | 1 | 1 | 4 | 44.9 | -3.2 | 3.3 | 0.9942 | 0.9364 | 0.9944 | 0.9263 | 0.1 | 0.79
8550 MARKHAM2A 69.0 8984 MRKHMTP2A 69.0 1 | 8550 | MARKHAM2A | 8984 | MRKHMTP2A | 1 | 69 | 8 | 61 | 61 | 5544 DANEVANGSW9 69.0 5548 DANEVANGSUB9 69.0 1 | 3504 | 33.6 | 63.2 | 98.62 | 103.58 | 1 | 0.97229 | 32.7 | 59.9 | -7.3 | -0.9 | 0.997 | 0.9481 | 0.9955 | 0.9418 | 0.54 | 1.01
5554 MARKHAMTAP9 69.0 8984 MRKHMTP2A 69.0 1 | 5554 | MARKHAMTAP9 | 8984 | MRKHMTP2A | 1 | 69 | 13/8 | 61 | 61 | 5544 DANEVANGSW9 69.0 5548 DANEVANGSUB9 69.0 1 | 3504 | 32.9 | 62.4 | 97.2 | 102.25 | 1 | 0.97499 | -31.7 | -58.3 | 7.8 | 2.8 | 0.9942 | 0.9364 | 0.9955 | 0.9418 | 0.48 | 0.91
8119 BLESSING2A 69.0 8550 MARKHAM2A 69.0 1 | 8119 | BLESSING2A | 8550 | MARKHAM2A | 1 | 69 | 8 | 61 | 61 | 5548 DANEVANGSUB9 69.0 5550 NCLEMVILSUB9 69.0 1 | 3507 | 36.7 | 59.7 | 96.02 | 97.87 | 2 | 0.84557 | 36.8 | 59.6 | -4.6 | 2.1 | 1.0104 | 0.9983 | 0.997 | 0.9637 | 3.21 | 5.11
8550 MARKHAM2A 69.0 8984 MRKHMTP2A 69.0 1 | 8550 | MARKHAM2A | 8984 | MRKHMTP2A | 1 | 69 | 8 | 61 | 61 | 5548 DANEVANGSUB9 69.0 5550 NCLEMVILSUB9 69.0 1 | 3507 | 33.6 | 56.3 | 89.07 | 92.32 | 2 | 0.97229 | 32.7 | 54.1 | -7.3 | -3.8 | 0.997 | 0.9637 | 0.9955 | 0.9589 | 0.54 | 0.9
5554 MARKHAMTAP9 69.0 8984 MRKHMTP2A 69.0 1 | 5554 | MARKHAMTAP9 | 8984 | MRKHMTP2A | 1 | 69 | 13/8 | 61 | 61 | 5548 DANEVANGSUB9 69.0 5550 NCLEMVILSUB9 69.0 1 | 3507 | 32.9 | 55.5 | 87.65 | 91.02 | 2 | 0.97499 | -31.7 | -52.7 | 7.8 | 5.3 | 0.9942 | 0.9548 | 0.9955 | 0.9589 | 0.48 | 0.81
8119 BLESSING2A 69.0 8550 MARKHAM2A 69.0 1 | 8119 | BLESSING2A | 8550 | MARKHAM2A | 1 | 69 | 8 | 61 | 61 | 5550 NCLEMVILSUB9 69.0 5559 TRESPALTAP9 69.0 1 | 3508 | 36.7 | 58.1 | 93.63 | 95.33 | 3 | 0.84557 | 36.8 | 58.1 | -4.6 | 1.2 | 1.0104 | 0.9997 | 0.997 | 0.9671 | 3.21 | 4.99
5554 MARKHAMTAP9 69.0 5558 VANVLECKSUB9 69.0 1 | 5554 | MARKHAMTAP9 | 5558 | VANVLECKSUB9 | 1 | 69 | 13 | 40 | 45 | 5574 OLIVIASW9 69.0 5580 VANHUMBLESW9 69.0 1 | 3527 | 28.3 | 44 | 93.52 | 97.78 | 2 | 0.84422 | 27.7 | 42.9 | -4.6 | -6 | 0.9942 | 0.9846 | 0.9833 | 0.9668 | 2.96 | 4.66
5554 MARKHAMTAP9 69.0 5558 VANVLECKSUB9 69.0 1 | 5554 | MARKHAMTAP9 | 5558 | VANVLECKSUB9 | 1 | 69 | 13 | 40 | 45 | 5580 VANHUMBLESW9 69.0 5582 VANDERBLTSW9 69.0 1 | 3529 | 28.3 | 44 | 94.95 | 97.89 | 1 | 0.84422 | 27.7 | 42.9 | -4.6 | -6.2 | 0.9942 | 0.985 | 0.9833 | 0.9676 | 2.96 | 4.67
8536 PV_TAP2A 69.0 80135 CSDBUS2 69.0 1 | 8536 | PV_TAP2A | 80135 | CSDBUS2 | 1 | 69 | 8 | 61 | 61 | 5598 SEADRIFTSUB9 69.0 80135 CSDBUS2 69.0 1 | 3540 | 44.6 | 55.3 | 88.77 | 90.61 | 1 | 0.63104 | -43.5 | -53.8 | 6.1 | 4.9 | 0.9864 | 0.9772 | 1.0066 | 1.0072 | 4.07 | 4.98
6338 BALLINGE2A 69.0 6340 BALLINGE4A 138 1 | 6338 | BALLINGE2A | 6340 | BALLINGE4A | 1 | 69/138 | 6 | 62.5 | 68.8 | 6326 ROBT2A 69.0 6327 CEDARGAP2A 69.0 1 | 4034 | 44.1 | 62.6 | 86.27 | 90.95 | 4 | 0.71055 | -43.5 | -62.1 | -4.5 | -1.3 | 0.9983 | 0.9976 | 1.0035 | 1.0011 | 3.01 | 4.33
6333 WINT2A 69.0 60332 STMBOAT2A 69.0 1 | 6333 | WINT2A | 60332 | STMBOAT2A | 1 | 69 | 6 | 25 | 25 | 6327 CEDARGAP2A 69.0 6636 ABSO2B 69.0 1 | 4036 | 8.8 | 26.1 | 95.49 | 104.48 | 1 | 1 | -8.2 | 25 | 2.6 | -4.9 | 0.9853 | 0.9772 | 0.9903 | 0.957 | 1.06 | 3.15
6331 CLIM2A 69.0 60332 STMBOAT2A 69.0 1 | 6331 | CLIM2A | 60332 | STMBOAT2A | 1 | 69 | 6 | 25 | 25 | 6327 CEDARGAP2A 69.0 6636 ABSO2B 69.0 1 | 4036 | 10.5 | 24.3 | 87.94 | 97.2 | 1 | 1 | 10 | -22.4 | -2.5 | 6.1 | 0.9905 | 0.9566 | 0.9903 | 0.957 | 0.03 | 0.07
6338 BALLINGE2A 69.0 6340 BALLINGE4A 138 1 | 6338 | BALLINGE2A | 6340 | BALLINGE4A | 1 | 69/138 | 6 | 62.5 | 68.8 | 6327 CEDARGAP2A 69.0 6636 ABSO2B 69.0 1 | 4036 | 44.1 | 66.2 | 90.66 | 96.22 | 1 | 0.71055 | -43.5 | -65.3 | -4.5 | -4 | 0.9983 | 0.9909 | 1.0035 | 0.9983 | 3.01 | 4.59
6338 BALLINGE2A 69.0 6340 BALLINGE4A 138 1 | 6338 | BALLINGE2A | 6340 | BALLINGE4A | 1 | 69/138 | 6 | 62.5 | 68.8 | 6340 BALLINGE4A 138 6360 COLE_IVI4A 138 1 | 4049 | 44.1 | 64.6 | 95.95 | 93.87 | 3 | 0.69024 | -43.5 | -64.2 | -4.5 | -0.7 | 0.9983 | 1.0129 | 1.0035 | 1.0158 | 3.01 | 4.34
6338 BALLINGE2A 69.0 6340 BALLINGE4A 138 1 | 6338 | BALLINGE2A | 6340 | BALLINGE4A | 1 | 69/138 | 6 | 62.5 | 68.8 | 6347 COLETAP4 138 6360 COLE_IVI4A 138 1 | 4060 | 44.1 | 64.8 | 94.86 | 94.25 | 2 | 0.69024 | -43.5 | -64.3 | -4.5 | -1.8 | 0.9983 | 1.0143 | 1.0035 | 1.0185 | 3.01 | 4.33
6450 CONCHO2A 69.0 6527 SANW2A 69.0 1 | 6450 | CONCHO2A | 6527 | SANW2A | 1 | 69 | 6 | 30 | 30 | 6490 SANTIAGO4A 138 6500 LVOK4A 138 1 | 4193 | 12.6 | 28.3 | 94.78 | 94.47 | 1 | 0.90327 | 12.5 | 28.8 | 2.4 | -1 | 1.0179 | 1.0168 | 1.0111 | 1.0079 | 0.65 | 1.63
6533 BIGLAKE2A 69.0 6546 PHBL_TAP2A 69.0 1 | 6533 | BIGLAKE2A | 6546 | PHBL_TAP2A | 1 | 69 | 6 | 38 | 38 | 6550 FDRAN2A 69.0 6560 OZONA2A 69.0 1 | 4242 | 27.5 | 40 | 102.61 | 105.32 | 1 | 0.86819 | 27.6 | 39.9 | 6.7 | 9.9 | 1.0328 | 1.0275 | 1.022 | 1.0119 | 1.31 | 1.92
6546 PHBL_TAP2A 69.0 6547 STRS2A 69.0 1 | 6546 | PHBL_TAP2A | 6547 | STRS2A | 1 | 69 | 6 | 38 | 38 | 6550 FDRAN2A 69.0 6560 OZONA2A 69.0 1 | 4242 | 27.3 | 39.8 | 101.7 | 104.82 | 1 | 0.94867 | 27.2 | 39.4 | 6.2 | 8.6 | 1.022 | 1.0119 | 1.0171 | 1.0049 | 0.5 | 0.75
6547 STRS2A 69.0 60395 BISON2A 69.0 1 | 6547 | STRS2A | 60395 | BISON2A | 1 | 69 | 6 | 38 | 38 | 6550 FDRAN2A 69.0 6560 OZONA2A 69.0 1 | 4242 | 24.5 | 36.9 | 93.89 | 97.21 | 1 | 0.91144 | 24.4 | 36.4 | 5.1 | 7.2 | 1.0171 | 1.0049 | 1.0107 | 0.9955 | 0.8 | 1.23
6666 ALPINE2A 69.0 6674 BRONCO2A 69.0 1 | 6666 | ALPINE2A | 6674 | BRONCO2A | 1 | 69 | 6 | 48 | 53 | 6630 FTST4A 138 60384 SOLSTICE4B 138 1 | 4299 | 42.2 | 54.4 | 95.32 | 102.62 | 1 | 0.84079 | -37.1 | -48.2 | 21.3 | 26.4 | 1.0181 | 1.0137 | 1.0095 | 1.0086 | 6.71 | 8.7
8293 LAREDO4A 138 8645 DEL_MAR4A 138 1 | 8293 | LAREDO4A | 8645 | DEL_MAR4A | 1 | 138 | 8 | 211 | 239 | 8112 LSCRUCES4A 138 8918 MILO4A 138 1 | 4888 | 160.1 | 232.9 | 98.82 | 97.43 | 2 | 0.94065 | 163.8 | 238.6 | 10.5 | 4.4 | 1.025 | 1.025 | 1.0211 | 1.0204 | 0.9 | 1.32
8293 LAREDO4A 138 8645 DEL_MAR4A 138 1 | 8293 | LAREDO4A | 8645 | DEL_MAR4A | 1 | 138 | 8 | 211 | 239 | 8112 LSCRUCES4A 138 80013 LARDVNTH4A 138 1 | 4889 | 160.1 | 238.3 | 101.12 | 99.73 | 1 | 0.94065 | 163.8 | 244.2 | 10.5 | 7.4 | 1.025 | 1.025 | 1.0211 | 1.0201 | 0.9 | 1.35
8133 BROOKHOL2A 69.0 8135 P_LAVACA2A 69.0 1 | 8133 | BROOKHOL2A | 8135 | P_LAVACA2A | 1 | 69 | 8 | 39 | 41 | 8121 BLESSING4A 138 8125 LOLITA4A 138 1 | 4899 | 31.1 | 37.2 | 87.31 | 90.75 | 1 | 0.95758 | -29.8 | -35.6 | 5.8 | 6.9 | 0.9788 | 0.9762 | 0.9841 | 0.9826 | 0.73 | 0.88
8536 PV_TAP2A 69.0 80135 CSDBUS2 69.0 1 | 8536 | PV_TAP2A | 80135 | CSDBUS2 | 1 | 69 | 8 | 61 | 61 | 8136 PLACEDO2A 69.0 8169 VICTORIA2A 69.0 1 | 4916 | 44.6 | 56.5 | 90.37 | 92.69 | 1 | 0.61017 | -43.5 | -54.7 | 6.1 | 8 | 0.9864 | 0.9786 | 1.0066 | 1.0045 | 4.07 | 5.18
8255 HAMILTON4A 138 8692 MAVERICK4A 138 1 | 8255 | HAMILTON4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8260 ESCONDID4A 138 78015 L_ROSICR8_1Y 138 1 | 5027 | 73.2 | 116.1 | 91.82 | 95.14 | 5 | 1 | 74.6 | 119 | -10.4 | -11.9 | 1.03 | 1.03 | 1.0044 | 0.9917 | 7.49 | 12.03
8267 GANSO4A 138 8692 MAVERICK4A 138 1 | 8267 | GANSO4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8260 ESCONDID4A 138 78015 L_ROSICR8_1Y 138 1 | 5027 | 69.8 | 112.8 | 86.56 | 92.42 | 5 | 1 | -68 | -106.7 | 16.4 | 32.9 | 1.0034 | 0.9909 | 1.0044 | 0.9917 | 0.42 | 0.7
8260 ESCONDID4A 138 8267 GANSO4A 138 1 | 8260 | ESCONDID4A | 8267 | GANSO4A | 1 | 138 | 8 | 122 | 122 | 8260 ESCONDID4A 138 78015 L_ROSICR8_1Y 138 1 | 5027 | 69.7 | 112.7 | 85.76 | 92.36 | 5 | 1 | -67.2 | -104.6 | 17.4 | 37.3 | 0.9996 | 0.9886 | 1.0034 | 0.9909 | 1.81 | 2.98
8255 HAMILTON4A 138 8692 MAVERICK4A 138 1 | 8255 | HAMILTON4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8273 PUEBLO4A 138 8274 W_CONOCO4A 138 1 | 5034 | 73.2 | 176.5 | 125.01 | 144.65 | 2 | 1 | 74.6 | 174.7 | -10.4 | 48.1 | 1.03 | 1.03 | 1.0044 | 0.8733 | 7.49 | 17.47
8267 GANSO4A 138 8692 MAVERICK4A 138 1 | 8267 | GANSO4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8273 PUEBLO4A 138 8274 W_CONOCO4A 138 1 | 5034 | 69.8 | 173.2 | 119.75 | 141.94 | 2 | 1 | -68 | -150 | 16.4 | 6 | 1.0034 | 0.8672 | 1.0044 | 0.8733 | 0.42 | 1.16
8260 ESCONDID4A 138 8267 GANSO4A 138 1 | 8260 | ESCONDID4A | 8267 | GANSO4A | 1 | 138 | 8 | 122 | 122 | 8273 PUEBLO4A 138 8274 W_CONOCO4A 138 1 | 5034 | 69.7 | 173.2 | 118.95 | 141.93 | 2 | 1 | -67.2 | -145.2 | 17.4 | 18 | 0.9996 | 0.8451 | 1.0034 | 0.8672 | 1.81 | 5.09
8255 HAMILTON4A 138 8692 MAVERICK4A 138 1 | 8255 | HAMILTON4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8273 PUEBLO4A 138 78015 L_ROSICR8_1Y 138 1 | 5035 | 73.2 | 126.3 | 99.24 | 103.52 | 3 | 1 | 74.6 | 130 | -10.4 | -4.7 | 1.03 | 1.03 | 1.0044 | 0.976 | 7.49 | 13.07
8267 GANSO4A 138 8692 MAVERICK4A 138 1 | 8267 | GANSO4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8273 PUEBLO4A 138 78015 L_ROSICR8_1Y 138 1 | 5035 | 69.8 | 123.1 | 93.98 | 100.89 | 3 | 1 | -68 | -116 | 16.4 | 30.4 | 1.0034 | 0.9745 | 1.0044 | 0.976 | 0.42 | 0.77
8260 ESCONDID4A 138 8267 GANSO4A 138 1 | 8260 | ESCONDID4A | 8267 | GANSO4A | 1 | 138 | 8 | 122 | 122 | 8273 PUEBLO4A 138 78015 L_ROSICR8_1Y 138 1 | 5035 | 69.7 | 123 | 93.18 | 100.84 | 3 | 1 | -67.2 | -113.5 | 17.4 | 35.8 | 0.9996 | 0.9698 | 1.0034 | 0.9745 | 1.81 | 3.3
8255 HAMILTON4A 138 8692 MAVERICK4A 138 1 | 8255 | HAMILTON4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8274 W_CONOCO4A 138 78281 L_DIMMIT8_1Y 138 1 | 5037 | 73.2 | 178.7 | 126.85 | 146.51 | 1 | 1 | 74.6 | 176.9 | -10.4 | 49 | 1.03 | 1.03 | 1.0044 | 0.8715 | 7.49 | 17.72
8267 GANSO4A 138 8692 MAVERICK4A 138 1 | 8267 | GANSO4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8274 W_CONOCO4A 138 78281 L_DIMMIT8_1Y 138 1 | 5037 | 69.8 | 175.4 | 121.58 | 143.8 | 1 | 1 | -68 | -151.7 | 16.4 | 6.6 | 1.0034 | 0.8654 | 1.0044 | 0.8715 | 0.42 | 1.18
8260 ESCONDID4A 138 8267 GANSO4A 138 1 | 8260 | ESCONDID4A | 8267 | GANSO4A | 1 | 138 | 8 | 122 | 122 | 8274 W_CONOCO4A 138 78281 L_DIMMIT8_1Y 138 1 | 5037 | 69.7 | 175.4 | 120.78 | 143.79 | 1 | 1 | -67.2 | -146.7 | 17.4 | 18.9 | 0.9996 | 0.8433 | 1.0034 | 0.8654 | 1.81 | 5.17
8255 HAMILTON4A 138 8692 MAVERICK4A 138 1 | 8255 | HAMILTON4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8283 ASHERTON4A 138 78280 L_BEVO__8_1Y 138 1 | 5044 | 73.2 | 117.4 | 92.09 | 96.22 | 4 | 0.8204 | 74.6 | 120.6 | -10.4 | 8.3 | 1.03 | 1.03 | 1.0044 | 0.9552 | 7.49 | 11.87
8267 GANSO4A 138 8692 MAVERICK4A 138 1 | 8267 | GANSO4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 8283 ASHERTON4A 138 78280 L_BEVO__8_1Y 138 1 | 5044 | 69.8 | 114.4 | 86.83 | 93.78 | 4 | 0.98961 | -68 | -108.1 | 16.4 | 13.6 | 1.0034 | 0.9522 | 1.0044 | 0.9552 | 0.42 | 0.72
8260 ESCONDID4A 138 8267 GANSO4A 138 1 | 8260 | ESCONDID4A | 8267 | GANSO4A | 1 | 138 | 8 | 122 | 122 | 8283 ASHERTON4A 138 78280 L_BEVO__8_1Y 138 1 | 5044 | 69.7 | 114.4 | 86.03 | 93.75 | 4 | 0.95581 | -67.2 | -105.9 | 17.4 | 18.2 | 0.9996 | 0.941 | 1.0034 | 0.9522 | 1.81 | 3.09
8112 LSCRUCES4A 138 80013 LARDVNTH4A 138 1 | 8112 | LSCRUCES4A | 80013 | LARDVNTH4A | 1 | 138 | 8 | 245 | 257 | 8293 LAREDO4A 138 8645 DEL_MAR4A 138 1 | 5050 | 161.1 | 245.6 | 95.53 | 95.58 | 1 | 0.99007 | -163.6 | -248.3 | -22 | -39.4 | 1.0243 | 1.0236 | 1.0251 | 1.0249 | 0.14 | 0.21
8112 LSCRUCES4A 138 8918 MILO4A 138 1 | 8112 | LSCRUCES4A | 8918 | MILO4A | 1 | 138 | 8 | 245 | 257 | 8293 LAREDO4A 138 8645 DEL_MAR4A 138 1 | 5050 | 149.8 | 234.3 | 91.03 | 91.16 | 1 | 0.94536 | 152.3 | 237.1 | 18.3 | 35.7 | 1.0243 | 1.0236 | 1.0204 | 1.0171 | 0.73 | 1.13
8295 WORMSER4A 138 8653 ST_NINO4A 138 1 | 8295 | WORMSER4A | 8653 | ST_NINO4A | 1 | 138 | 8 | 216 | 244 | 8293 LAREDO4A 138 8645 DEL_MAR4A 138 1 | 5050 | 51.9 | 220.7 | 87.44 | 90.47 | 1 | 1 | 49.6 | 215.1 | 17.9 | 32.1 | 1.0172 | 0.9853 | 1.0141 | 0.9771 | 0.3 | 1.44
8483 SOUTH_SI4A 138 8486 HOLLY4A 138 1 | 8483 | SOUTH_SI4A | 8486 | HOLLY4A | 1 | 138 | 8 | 211 | 211 | 8485 WESTSIDE4A 138 8486 HOLLY4A 138 1 | 5251 | 152.9 | 219.9 | 105.62 | 104.21 | 1 | 0.86214 | -154.9 | -221.7 | 20.2 | 35.6 | 1.022 | 1.0214 | 1.0226 | 1.0218 | 0.58 | 0.83
8483 SOUTH_SI4A 138 8486 HOLLY4A 138 1 | 8483 | SOUTH_SI4A | 8486 | HOLLY4A | 1 | 138 | 8 | 211 | 211 | 8485 WESTSIDE4A 138 8882 CABANISS4A 138 1 | 5254 | 152.9 | 193.8 | 93.27 | 91.84 | 3 | 0.82146 | -154.9 | -196 | 20.2 | 28.4 | 1.022 | 1.022 | 1.0226 | 1.0226 | 0.58 | 0.73
8486 HOLLY4A 138 8517 HOLLY4B 138 BT | 8486 | HOLLY4A | 8517 | HOLLY4B | BT | 138 | 8 | 478 | 478 | 8485 WESTSIDE4A 138 8882 CABANISS4A 138 1 | 5254 | 320.9 | 434.8 | 92.13 | 90.97 | 2 | 0.99912 | -324.9 | -440.1 | 46.4 | 63.4 | 1.0226 | 1.0226 | 1.0226 | 1.0225 | 0.02 | 0.02
8483 SOUTH_SI4A 138 8486 HOLLY4A 138 1 | 8483 | SOUTH_SI4A | 8486 | HOLLY4A | 1 | 138 | 8 | 211 | 211 | 8490 AIRLINE4A 138 8882 CABANISS4A 138 1 | 5260 | 152.9 | 201.5 | 97.12 | 95.49 | 2 | 0.82146 | -154.9 | -203.9 | 20.2 | 28.4 | 1.022 | 1.0219 | 1.0226 | 1.0226 | 0.58 | 0.76
8486 HOLLY4A 138 8517 HOLLY4B 138 BT | 8486 | HOLLY4A | 8517 | HOLLY4B | BT | 138 | 8 | 478 | 478 | 8490 AIRLINE4A 138 8882 CABANISS4A 138 1 | 5260 | 320.9 | 455.8 | 96.82 | 95.36 | 1 | 0.99912 | -324.9 | -462.1 | 46.4 | 61.2 | 1.0226 | 1.0226 | 1.0226 | 1.0225 | 0.02 | 0.03
8427 ARANSASP2A 69.0 8435 SEAWALL2A 69.0 1 | 8427 | ARANSASP2A | 8435 | SEAWALL2A | 1 | 69 | 8 | 76 | 76 | 8495 NAVALBS2A 69.0 8856 N_PADRE2A 69.0 1 | 5263 | 17.4 | 77.2 | 102.84 | 101.55 | 1 | 1 | 17.2 | 78.5 | 2.8 | -9.2 | 1.0036 | 1.0241 | 0.9993 | 1.02 | 0.62 | 2.9
8565 HECKER4A 138 8961 WHITEPT4A 138 2 | 8565 | HECKER4A | 8961 | WHITEPT4A | 2 | 138 | 8 | 211 | 239 | 8565 HECKER4A 138 8961 WHITEPT4A 138 1 | 5310 | 164.1 | 244 | 101.3 | 102.08 | 1 | 0.51355 | -163.3 | -241.7 | -27.8 | -38.9 | 1.0098 | 1.0035 | 1.0222 | 1.0218 | 1.85 | 2.76
8565 HECKER4A 138 8961 WHITEPT4A 138 1 | 8565 | HECKER4A | 8961 | WHITEPT4A | 1 | 138 | 8 | 211 | 239 | 8565 HECKER4A 138 8961 WHITEPT4A 138 2 | 5311 | 154.1 | 236.6 | 98.19 | 99 | 1 | 0.49778 | -153.4 | -234.3 | -26.2 | -37.7 | 1.0098 | 1.0029 | 1.0222 | 1.0218 | 1.85 | 2.85
8293 LAREDO4A 138 8645 DEL_MAR4A 138 1 | 8293 | LAREDO4A | 8645 | DEL_MAR4A | 1 | 138 | 8 | 211 | 239 | 8641 SIEVISTA4A 138 80230 MOLINA4A 138 1 | 5335 | 160.1 | 217.2 | 92.74 | 90.88 | 3 | 0.94287 | 163.8 | 222.4 | 10.5 | 9.6 | 1.025 | 1.025 | 1.0211 | 1.0202 | 0.9 | 1.23
8422 I_DUPSW4A 138 8819 I_DUPP14B 138 2 | 8422 | I_DUPSW4A | 8819 | I_DUPP14B | 2 | 138 | 8 | 211 | 211 | 8818 OXY_INGL4A 138 8968 INGLCOSW4A 138 2 | 5370 | 85.2 | 196.8 | 85.59 | 93.25 | 1 | 0.55824 | -75 | -180.3 | -43.1 | -85.9 | 1.0158 | 1.015 | 1.0189 | 1.0214 | 0.2 | 0.49
80013 LARDVNTH4A 138 80165 LARDVFT4A 138 1 | 80013 | LARDVNTH4A | 80165 | LARDVFT4A | 1 | 138 | 8 | 209 | 246 | 8825 SURRCFE4 138 86107 CUF-138 138 1 | 5379 | 98.1 | 224.4 | 80.77 | 91.2 | 1 | 1 | 100.2 | -223.5 | 7.9 | 54.1 | 1.0251 | 1.0252 | 1.0249 | 1.0251 | 0.04 | 0.08
6666 ALPINE2A 69.0 6674 BRONCO2A 69.0 1 | 6666 | ALPINE2A | 6674 | BRONCO2A | 1 | 69 | 6 | 48 | 53 | 11245 WARD1927_8 138 60397 GASPADTA4A 138 1 | 5622 | 42.2 | 49 | 84 | 92.54 | 1 | 0.83133 | -37.1 | -43.7 | 21.3 | 23.1 | 1.0181 | 1.0121 | 1.0095 | 1.0084 | 6.71 | 7.85
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 12734 CHIESA2_8 138 12736 ROWLETT_T8 138 1 | 5681 | 193.6 | 233.8 | 106.93 | 107.25 | 1 | 0.80142 | 194.1 | 234.1 | 14 | 16.6 | 1.0055 | 1.0038 | 0.999 | 0.9961 | 1.6 | 1.93
802 APOLLO 138 825 NAAMAN 138 1 | 802 | APOLLO | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 12734 CHIESA2_8 138 12736 ROWLETT_T8 138 1 | 5681 | 170.8 | 210.9 | 96.04 | 96.75 | 1 | 0.70698 | -169.5 | -208.4 | 1.2 | 4.3 | 0.9923 | 0.9883 | 0.999 | 0.9961 | 2.11 | 2.62
38230 TNAAPIPLNT0 69.0 38231 TNAAPIPLNM0 69.0 1 | 38230 | TNAAPIPLNT0 | 38231 | TNAAPIPLNM0 | 1 | 69 | 17 | 43 | 43 | 37920 TNWINK____0 69.0 38230 TNAAPIPLNT0 69.0 1 | 5843 | 35.1 | 41.4 | 76.9 | 96.28 | 1 | 1 | 33.1 | 33.1 | 11 | 11.1 | 0.9933 | 0.8429 | 0.9921 | 0.8415 | 0.05 | 0.07
110382 EXN_1_8 138 110384 EXN_3_8 138 SG | 110382 | EXN_1_8 | 110384 | EXN_3_8 | SG | 138 | 904/4 | 215 | 240 | 40570 EXXON__POI_8 138 110383 EXN_2_8 138 SG | 6170 | 47.6 | 232.4 | 89.58 | 96.84 | 1 | 1 | 42 | 215.1 | 25.2 | 114.1 | 1.0295 | 1.0478 | 1.026 | 1.0326 | 0.27 | 1.37
40570 EXXON__POI_8 138 110384 EXN_3_8 138 SG | 40570 | EXXON__POI_8 | 110384 | EXN_3_8 | SG | 138 | 4 | 215 | 240 | 40570 EXXON__POI_8 138 110383 EXN_2_8 138 SG | 6170 | 42 | 226.8 | 87.48 | 94.52 | 1 | 1 | -37 | -209.1 | -22 | -101 | 1.0241 | 1.0234 | 1.026 | 1.0326 | 0.13 | 0.73
40570 EXXON__POI_8 138 110383 EXN_2_8 138 SG | 40570 | EXXON__POI_8 | 110383 | EXN_2_8 | SG | 138 | 4/904 | 215 | 240 | 40570 EXXON__POI_8 138 110384 EXN_3_8 138 SG | 6171 | 189.9 | 231.5 | 87.48 | 96.48 | 1 | 1 | -173 | -209.9 | -88.8 | -110.3 | 1.0241 | 1.0241 | 1.0272 | 1.0278 | 0.24 | 0.28
110127 DOWGEN_2_8 138 110128 DOWGEN_3_8 138 SG | 110127 | DOWGEN_2_8 | 110128 | DOWGEN_3_8 | SG | 138 | 904 | 120 | 120 | 42514 DOW____POI8A 138 110133 DOWGEN_6_8 138 1 | 6372 | 109 | 112.5 | 85.06 | 93.72 | 1 | 1 | 102.1 | 102 | 26.1 | 24.6 | 0.9667 | 0.9332 | 0.9665 | 0.9331 | 0.02 | 0.02
110127 DOWGEN_2_8 138 110128 DOWGEN_3_8 138 SG | 110127 | DOWGEN_2_8 | 110128 | DOWGEN_3_8 | SG | 138 | 904 | 120 | 120 | 42515 DOW____POI8B 138 110133 DOWGEN_6_8 138 1 | 6373 | 109 | 112.3 | 85.06 | 93.54 | 2 | 1 | 102.1 | 102 | 26.1 | 24.7 | 0.9667 | 0.9353 | 0.9665 | 0.9351 | 0.02 | 0.02
45730 DEIHL__S81_8 138 46610 WHITOK_B138A 138 81 | 45730 | DEIHL__S81_8 | 46610 | WHITOK_B138A | 81 | 138 | 4 | 382 | 382 | 45511 T_H_W_81T5_8 138 45515 T_H_W__POI_8 138 81 | 6646 | 29.7 | 383.1 | 96.47 | 100.28 | 1 | 1 | 18 | -368.4 | -24.4 | -103.6 | 1.0193 | 0.999 | 1.0227 | 1.0203 | 0.16 | 3.06
44120 BRITMR__B138 138 44311 HAYES_24T3_8 138 24 | 44120 | BRITMR__B138 | 44311 | HAYES_24T3_8 | 24 | 138 | 4 | 227 | 290 | 47010 BELAIR_B138A 138 47012 BELAIR24T6_8 138 24 | 6744 | 13.2 | 318.5 | 105.26 | 109.84 | 1 | 1 | 10.9 | 309.9 | 7.5 | 89.9 | 1.0191 | 1.0134 | 1.0179 | 0.9954 | 0.07 | 2.1
44311 HAYES_24T3_8 138 44762 WCHASE24T3_8 138 24 | 44311 | HAYES_24T3_8 | 44762 | WCHASE24T3_8 | 24 | 138 | 4 | 227 | 290 | 47010 BELAIR_B138A 138 47012 BELAIR24T6_8 138 24 | 6744 | 14.1 | 292.8 | 96.62 | 100.96 | 1 | 1 | -14.1 | 282.4 | 2 | 71.6 | 1.0179 | 0.9954 | 1.0179 | 0.9815 | 0.09 | 1.8
6666 ALPINE2A 69.0 6674 BRONCO2A 69.0 1 | 6666 | ALPINE2A | 6674 | BRONCO2A | 1 | 69 | 6 | 48 | 53 | 60384 SOLSTICE4B 138 60385 SOLSTICE4A 138 1 | 6862 | 42.2 | 54.4 | 94.52 | 102.63 | 1 | 0.84079 | -37.1 | -48.2 | 21.3 | 26.4 | 1.0181 | 1.0137 | 1.0095 | 1.0087 | 6.71 | 8.7
6666 ALPINE2A 69.0 6674 BRONCO2A 69.0 1 | 6666 | ALPINE2A | 6674 | BRONCO2A | 1 | 69 | 6 | 48 | 53 | 60397 GASPADTA4A 138 60415 BASIN4A 138 1 | 6873 | 42.2 | 47.8 | 81.2 | 90.15 | 2 | 0.83133 | -37.1 | -42.3 | 21.3 | 23.2 | 1.0181 | 1.0146 | 1.0095 | 1.0088 | 6.71 | 7.63
8255 HAMILTON4A 138 8692 MAVERICK4A 138 1 | 8255 | HAMILTON4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 78280 L_BEVO__8_1Y 138 78281 L_DIMMIT8_1Y 138 1 | 7011 | 73.2 | 199.2 | 137.86 | 163.26 | 1 | 1 | 74.6 | 190.1 | -10.4 | 74.6 | 1.03 | 1.03 | 1.0044 | 0.8242 | 7.49 | 19.2
8260 ESCONDID4A 138 8267 GANSO4A 138 1 | 8260 | ESCONDID4A | 8267 | GANSO4A | 1 | 138 | 8 | 122 | 122 | 78280 L_BEVO__8_1Y 138 78281 L_DIMMIT8_1Y 138 1 | 7011 | 69.7 | 195.6 | 131.8 | 160.33 | 1 | 1 | -67.2 | -153.3 | 17.4 | 10.8 | 0.9996 | 0.7857 | 1.0034 | 0.8159 | 1.81 | 6.02
8267 GANSO4A 138 8692 MAVERICK4A 138 1 | 8267 | GANSO4A | 8692 | MAVERICK4A | 1 | 138 | 8 | 122 | 122 | 78280 L_BEVO__8_1Y 138 78281 L_DIMMIT8_1Y 138 1 | 7011 | 69.8 | 195.6 | 132.6 | 160.33 | 1 | 1 | -68 | -159.5 | 16.4 | -4.8 | 1.0034 | 0.8159 | 1.0044 | 0.8242 | 0.42 | 1.35
110127 DOWGEN_2_8 138 110128 DOWGEN_3_8 138 SG | 110127 | DOWGEN_2_8 | 110128 | DOWGEN_3_8 | SG | 138 | 904 | 120 | 120 | 110133 DOWGEN_6_8 138 110149 DOW_1_8 138 1 | 7202 | 109 | 112.5 | 85.06 | 93.73 | 1 | 1 | 102.1 | 102 | 26.1 | 24.6 | 0.9667 | 0.9332 | 0.9665 | 0.933 | 0.02 | 0.02
110377 EXN_1_9 69.0 110378 EXN_2_9 69.0 SG | 110377 | EXN_1_9 | 110378 | EXN_2_9 | SG | 69 | 904 | 167 | 185 | 110377 EXN_1_9 69.0 110378 EXN_2_9 69.0 SH | 7219 | 134.8 | 172.4 | 82.1 | 93.21 | 1 | 0.83932 | -119.3 | -151.9 | -57.3 | -74.1 | 0.9817 | 0.9803 | 0.9858 | 0.9857 | 0.3 | 0.38
40570 EXXON__POI_8 138 110383 EXN_2_8 138 SG | 40570 | EXXON__POI_8 | 110383 | EXN_2_8 | SG | 138 | 4/904 | 215 | 240 | 110382 EXN_1_8 138 110384 EXN_3_8 138 SG | 7224 | 189.9 | 237.1 | 89.58 | 98.78 | 1 | 1 | -173 | -214.9 | -88.8 | -113 | 1.0241 | 1.0241 | 1.0272 | 1.0279 | 0.24 | 0.29
110464 FORMOSA_11_9 69.0 8126 FORMOSA4A 138 1 | 110464 | FORMOSA_11_9 | 8126 | FORMOSA4A | 1 | 69/138 | 908/8 | 133 | 133 | 110441 FORMOSA_1_9 69.0 110463 FORMOSA_10_9 69.0 BC | 7225 | 86.9 | 154.3 | 102.78 | 116.03 | 4 | 0.64547 | -79.3 | -137.8 | -27.3 | -44 | 0.9759 | 0.9473 | 1.0109 | 1.0109 | 25.29 | 21.54
110463 FORMOSA_10_9 69.0 110466 FORMOSA_13_9 69.0 1 | 110463 | FORMOSA_10_9 | 110466 | FORMOSA_13_9 | 1 | 69 | 908 | 136.2 | 136.2 | 110441 FORMOSA_1_9 69.0 110463 FORMOSA_10_9 69.0 BC | 7225 | 86.9 | 154.3 | 101.15 | 113.29 | 4 | 0.8484 | -79.8 | -137.8 | -24.1 | -33.7 | 0.9591 | 0.9196 | 0.9774 | 0.9499 | 2.04 | 3.82
110466 FORMOSA_13_9 69.0 8126 FORMOSA4A 138 2 | 110466 | FORMOSA_13_9 | 8126 | FORMOSA4A | 2 | 69/138 | 908/8 | 149 | 149 | 110441 FORMOSA_1_9 69.0 110463 FORMOSA_10_9 69.0 BC | 7225 | 87.8 | 156 | 92.89 | 104.71 | 4 | 0.65433 | -80.4 | -139.7 | -27.4 | -44.2 | 0.9774 | 0.9499 | 1.0109 | 1.0109 | 25.34 | 21.64
110463 FORMOSA_10_9 69.0 110464 FORMOSA_11_9 69.0 1 | 110463 | FORMOSA_10_9 | 110464 | FORMOSA_11_9 | 1 | 69 | 908 | 159 | 159 | 110441 FORMOSA_1_9 69.0 110463 FORMOSA_10_9 69.0 BC | 7225 | 86 | 152.7 | 85.66 | 96.01 | 4 | 0.8518 | -78.8 | -136.2 | -24.1 | -33.9 | 0.9591 | 0.9196 | 0.9759 | 0.9473 | 1.99 | 3.72
110464 FORMOSA_11_9 69.0 8126 FORMOSA4A 138 1 | 110464 | FORMOSA_11_9 | 8126 | FORMOSA4A | 1 | 69/138 | 908/8 | 133 | 133 | 110442 FORMOSA_2_9 69.0 110465 FORMOSA_12_9 69.0 BC | 7226 | 86.9 | 154.4 | 102.78 | 116.07 | 3 | 0.64547 | -79.3 | -137.8 | -27.3 | -44 | 0.9759 | 0.9472 | 1.0109 | 1.0109 | 25.29 | 21.54
110463 FORMOSA_10_9 69.0 110466 FORMOSA_13_9 69.0 1 | 110463 | FORMOSA_10_9 | 110466 | FORMOSA_13_9 | 1 | 69 | 908 | 136.2 | 136.2 | 110442 FORMOSA_2_9 69.0 110465 FORMOSA_12_9 69.0 BC | 7226 | 86.9 | 154.3 | 101.15 | 113.32 | 3 | 0.8484 | -79.8 | -137.8 | -24.1 | -33.8 | 0.9591 | 0.9194 | 0.9774 | 0.9498 | 2.04 | 3.82
110466 FORMOSA_13_9 69.0 8126 FORMOSA4A 138 2 | 110466 | FORMOSA_13_9 | 8126 | FORMOSA4A | 2 | 69/138 | 908/8 | 149 | 149 | 110442 FORMOSA_2_9 69.0 110465 FORMOSA_12_9 69.0 BC | 7226 | 87.8 | 156 | 92.89 | 104.74 | 3 | 0.65433 | -80.4 | -139.7 | -27.4 | -44.3 | 0.9774 | 0.9498 | 1.0109 | 1.0109 | 25.34 | 21.64
110463 FORMOSA_10_9 69.0 110464 FORMOSA_11_9 69.0 1 | 110463 | FORMOSA_10_9 | 110464 | FORMOSA_11_9 | 1 | 69 | 908 | 159 | 159 | 110442 FORMOSA_2_9 69.0 110465 FORMOSA_12_9 69.0 BC | 7226 | 86 | 152.7 | 85.66 | 96.04 | 3 | 0.8518 | -78.8 | -136.2 | -24.1 | -34 | 0.9591 | 0.9194 | 0.9759 | 0.9472 | 1.99 | 3.72
110464 FORMOSA_11_9 69.0 8126 FORMOSA4A 138 1 | 110464 | FORMOSA_11_9 | 8126 | FORMOSA4A | 1 | 69/138 | 908/8 | 133 | 133 | 110444 FORMOSA_4_9 69.0 110465 FORMOSA_12_9 69.0 BC | 7228 | 86.9 | 130.7 | 85.34 | 98.27 | 5 | 0.64547 | -79.3 | -114.1 | -27.3 | -45.4 | 0.9759 | 0.9502 | 1.0109 | 1.0109 | 25.29 | 23.04
110463 FORMOSA_10_9 69.0 110466 FORMOSA_13_9 69.0 1 | 110463 | FORMOSA_10_9 | 110466 | FORMOSA_13_9 | 1 | 69 | 908 | 136.2 | 136.2 | 110444 FORMOSA_4_9 69.0 110465 FORMOSA_12_9 69.0 BC | 7228 | 86.9 | 130.7 | 83.94 | 95.94 | 5 | 0.8484 | -79.8 | -114.4 | -24.1 | -38.2 | 0.9591 | 0.9229 | 0.9774 | 0.9525 | 2.04 | 3.09
110463 FORMOSA_10_9 69.0 110466 FORMOSA_13_9 69.0 1 | 110463 | FORMOSA_10_9 | 110466 | FORMOSA_13_9 | 1 | 69 | 908 | 136.2 | 136.2 | 110463 FORMOSA_10_9 69.0 110464 FORMOSA_11_9 69.0 1 | 7234 | 86.9 | 191 | 116.44 | 140.23 | 2 | 1 | -79.8 | -158.8 | -24.1 | -51.3 | 0.9591 | 0.8739 | 0.9774 | 0.9175 | 2.04 | 4.72
110466 FORMOSA_13_9 69.0 8126 FORMOSA4A 138 2 | 110466 | FORMOSA_13_9 | 8126 | FORMOSA4A | 2 | 69/138 | 908/8 | 149 | 149 | 110463 FORMOSA_10_9 69.0 110464 FORMOSA_11_9 69.0 1 | 7234 | 87.8 | 193.1 | 106.87 | 129.61 | 2 | 1 | -80.4 | -161.7 | -27.4 | -67.4 | 0.9774 | 0.9175 | 1.0109 | 1.0109 | 25.34 | 19.99
110464 FORMOSA_11_9 69.0 8126 FORMOSA4A 138 1 | 110464 | FORMOSA_11_9 | 8126 | FORMOSA4A | 1 | 69/138 | 908/8 | 133 | 133 | 110463 FORMOSA_10_9 69.0 110466 FORMOSA_13_9 69.0 1 | 7236 | 86.9 | 193.5 | 119.6 | 145.45 | 2 | 1 | -79.3 | -161.2 | -27.3 | -67.2 | 0.9759 | 0.913 | 1.0109 | 1.0109 | 25.29 | 19.75
110463 FORMOSA_10_9 69.0 110464 FORMOSA_11_9 69.0 1 | 110463 | FORMOSA_10_9 | 110464 | FORMOSA_11_9 | 1 | 69 | 908 | 159 | 159 | 110463 FORMOSA_10_9 69.0 110466 FORMOSA_13_9 69.0 1 | 7236 | 86 | 191.4 | 99.74 | 120.36 | 2 | 1 | -78.8 | -158.8 | -24.1 | -51.4 | 0.9591 | 0.8724 | 0.9759 | 0.913 | 1.99 | 4.69
1234 PGASUSTA_9 69.0 1276 PLESNTFARM_9 69.0 1 | 1234 | PGASUSTA_9 | 1276 | PLESNTFARM_9 | 1 | 69 | 1 | 42 | 42 | 1198 CRANE_9 69.0 1196 CRANE_8 138 1 | 7398 | 2.1 | 39.9 | 78.44 | 94.95 | 1 | 1 | -0.8 | 34.4 | 1.9 | 9.9 | 0.9902 | 0.8985 | 0.989 | 0.8657 | 0.11 | 1.86
1123 ODESSANO_9 69.0 1234 PGASUSTA_9 69.0 1 | 1123 | ODESSANO_9 | 1234 | PGASUSTA_9 | 1 | 69 | 1 | 42 | 42 | 1198 CRANE_9 69.0 1196 CRANE_8 138 1 | 7398 | 2 | 39.8 | 78.46 | 94.88 | 1 | 1 | -0.8 | 36.8 | 1.5 | 13.3 | 0.993 | 0.9856 | 0.9902 | 0.8985 | 0.26 | 4.19
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2355 RNRTPL1_5 345 3WXFMR AUTO1 1 | 7468 | 193.6 | 208.9 | 95.32 | 95.8 | 1 | 0.79637 | 194.1 | 209 | 14 | 17.4 | 1.0055 | 1.0041 | 0.999 | 0.9968 | 1.6 | 1.72
2975 INDUST_1T8 138 2976 INDUST_E8 138 1 | 2975 | INDUST_1T8 | 2976 | INDUST_E8 | 1 | 138 | 1 | 287 | 287 | 2398 WLEVEE1_5 345 3WXFMR AUTO2 2 | 7477 | 175.5 | 297.8 | 104.32 | 103.75 | 1 | 0.9952 | 177.2 | 300.1 | -20.1 | -37.9 | 1.0159 | 1.0158 | 1.0159 | 1.0158 | 0.01 | 0.02
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2513 ALLENSW1_5 345 3WXFMR AUTO1 1 | 7500 | 193.6 | 203.4 | 92.99 | 93.29 | 2 | 0.79622 | 194.1 | 203.7 | 14 | 15.3 | 1.0055 | 1.0047 | 0.999 | 0.9978 | 1.6 | 1.68
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2514 ALLENSW2_5 345 3WXFMR AUTO2 1 | 7501 | 193.6 | 202.5 | 93.45 | 92.9 | 3 | 0.79625 | 194.1 | 203.9 | 14 | 6.3 | 1.0055 | 1.0072 | 0.999 | 1.0016 | 1.6 | 1.68
823 WALNUT 138 825 NAAMAN 138 1 | 823 | WALNUT | 825 | NAAMAN | 1 | 138 | 20 | 218 | 218 | 2522 PL_TENNY_5 345 3WXFMR AUTO1 1 | 7502 | 193.6 | 201.5 | 91.94 | 92.42 | 4 | 0.79587 | 194.1 | 201.8 | 14 | 15.8 | 1.0055 | 1.0046 | 0.999 | 0.9977 | 1.6 | 1.66
6409 VRBS2A 69.0 6450 CONCHO2A 69.0 1 | 6409 | VRBS2A | 6450 | CONCHO2A | 1 | 69 | 6 | 30 | 30 | 6338 BALLINGE2A 69.0 6340 BALLINGE4A 138 1 | 7622 | 18.1 | 29.2 | 97.38 | 97.24 | 1 | 0.91807 | -18.2 | -29.4 | -1.4 | 1.1 | 1.0106 | 1.0084 | 1.0179 | 1.0184 | 0.56 | 0.98
6533 BIGLAKE2A 69.0 6546 PHBL_TAP2A 69.0 1 | 6533 | BIGLAKE2A | 6546 | PHBL_TAP2A | 1 | 69 | 6 | 38 | 38 | 6550 FDRAN2A 69.0 6562 FDRAN4A 138 1 | 7641 | 27.5 | 35.1 | 93.45 | 92.34 | 1 | 0.84598 | 27.6 | 35.4 | 6.7 | 7.3 | 1.0328 | 1.0303 | 1.022 | 1.0178 | 1.31 | 1.7
6546 PHBL_TAP2A 69.0 6547 STRS2A 69.0 1 | 6546 | PHBL_TAP2A | 6547 | STRS2A | 1 | 69 | 6 | 38 | 38 | 6550 FDRAN2A 69.0 6562 FDRAN4A 138 1 | 7641 | 27.3 | 34.9 | 92.54 | 91.84 | 1 | 0.94002 | 27.2 | 34.9 | 6.2 | 6.3 | 1.022 | 1.0178 | 1.0171 | 1.0121 | 0.5 | 0.66
8133 BROOKHOL2A 69.0 8135 P_LAVACA2A 69.0 1 | 8133 | BROOKHOL2A | 8135 | P_LAVACA2A | 1 | 69 | 8 | 39 | 41 | 8119 BLESSING2A 69.0 8121 BLESSING4A 138 1 | 7704 | 31.1 | 42.8 | 101.41 | 104.27 | 1 | 0.96392 | -29.8 | -41 | 5.8 | 1.1 | 0.9788 | 0.9601 | 0.9841 | 0.9702 | 0.73 | 0.94
110463 FORMOSA_10_9 69.0 110466 FORMOSA_13_9 69.0 1 | 110463 | FORMOSA_10_9 | 110466 | FORMOSA_13_9 | 1 | 69 | 908 | 136.2 | 136.2 | 110464 FORMOSA_11_9 69.0 8126 FORMOSA4A 138 1 | 7706 | 86.9 | 191 | 116.79 | 140.23 | 1 | 1 | -79.8 | -158.8 | -24.1 | -51.3 | 0.9591 | 0.8739 | 0.9774 | 0.9175 | 2.04 | 4.72
110466 FORMOSA_13_9 69.0 8126 FORMOSA4A 138 2 | 110466 | FORMOSA_13_9 | 8126 | FORMOSA4A | 2 | 69/138 | 908/8 | 149 | 149 | 110464 FORMOSA_11_9 69.0 8126 FORMOSA4A 138 1 | 7706 | 87.8 | 193.1 | 107.19 | 129.61 | 1 | 1 | -80.4 | -161.7 | -27.4 | -67.4 | 0.9774 | 0.9175 | 1.0109 | 1.0109 | 25.34 | 19.99
110464 FORMOSA_11_9 69.0 8126 FORMOSA4A 138 1 | 110464 | FORMOSA_11_9 | 8126 | FORMOSA4A | 1 | 69/138 | 908/8 | 133 | 133 | 110466 FORMOSA_13_9 69.0 8126 FORMOSA4A 138 2 | 7707 | 86.9 | 193.5 | 120.06 | 145.45 | 1 | 1 | -79.3 | -161.2 | -27.3 | -67.2 | 0.9759 | 0.913 | 1.0109 | 1.0109 | 25.29 | 19.75
110463 FORMOSA_10_9 69.0 110464 FORMOSA_11_9 69.0 1 | 110463 | FORMOSA_10_9 | 110464 | FORMOSA_11_9 | 1 | 69 | 908 | 159 | 159 | 110466 FORMOSA_13_9 69.0 8126 FORMOSA4A 138 2 | 7707 | 86 | 191.4 | 100.12 | 120.36 | 1 | 1 | -78.8 | -158.8 | -24.1 | -51.4 | 0.9591 | 0.8724 | 0.9759 | 0.913 | 1.99 | 4.69
8427 ARANSASP2A 69.0 8435 SEAWALL2A 69.0 1 | 8427 | ARANSASP2A | 8435 | SEAWALL2A | 1 | 69 | 8 | 76 | 76 | 8997 NAVALBS4A 138 8495 NAVALBS2A 69.0 1 | 7751 | 17.4 | 77.2 | 102.87 | 101.59 | 1 | 1 | 17.2 | 78.5 | 2.8 | -9.6 | 1.0036 | 1.0243 | 0.9993 | 1.0205 | 0.62 | 2.9
11084 RIVERTON_5 345 999814 AUTO2 138 2 | 11084 | RIVERTON_5 | 999814 | AUTO2 | 2 | 345/138 | 1 | 600 | 600 | 11084 RIVERTON_5 345 3WXFMR AUTO1 1 | 7774 | 370.1 | 629.2 | 104.48 | 104.87 | 1 | 0.66104 | 369.8 | 627.9 | 13.8 | 41.2 | 1.0208 | 1.0197 | 1.0204 | 1.0188 | 4.39 | 7.49
11083 RIVERTON_8 138 999814 AUTO2 138 2 | 11083 | RIVERTON_8 | 999814 | AUTO2 | 2 | 138 | 1 | 600 | 600 | 11084 RIVERTON_5 345 3WXFMR AUTO1 1 | 7774 | 369.7 | 627.8 | 104.42 | 104.63 | 1 | 1.0346 | -369.5 | -626.9 | 11.7 | 32.6 | 1.0197 | 1.0174 | 1.0204 | 1.0188 | 0.45 | 0.76
11084 RIVERTON_5 345 999815 AUTO1 138 1 | 11084 | RIVERTON_5 | 999815 | AUTO1 | 1 | 345/138 | 1 | 600 | 600 | 11084 RIVERTON_5 345 3WXFMR AUTO2 2 | 7775 | 370.1 | 629.2 | 104.48 | 104.87 | 1 | 0.66104 | 369.8 | 627.9 | 13.8 | 41.2 | 1.0208 | 1.0197 | 1.0204 | 1.0188 | 4.39 | 7.49
11083 RIVERTON_8 138 999815 AUTO1 138 1 | 11083 | RIVERTON_8 | 999815 | AUTO1 | 1 | 138 | 1 | 600 | 600 | 11084 RIVERTON_5 345 3WXFMR AUTO2 2 | 7775 | 369.7 | 627.8 | 104.42 | 104.63 | 1 | 1.0346 | -369.5 | -626.9 | 11.7 | 32.6 | 1.0197 | 1.0174 | 1.0204 | 1.0188 | 0.45 | 0.76
41400 S_R_B__POI8A 138 999785 30359 69.0 A1 | 41400 | S_R_B__POI8A | 999785 | 30359 | A1 | 138/69 | 4 | 200 | 210 | 41400 S_R_B__POI8A 138 3WXFMR D577567 A2 | 7829 | 122.7 | 189.5 | 89.48 | 90.26 | 1 | 0.72464 | -118.3 | -186.6 | 32.5 | 33.2 | 1.0147 | 1.013 | 0.9905 | 0.9904 | 2.8 | 4.43
110127 DOWGEN_2_8 138 110128 DOWGEN_3_8 138 SG | 110127 | DOWGEN_2_8 | 110128 | DOWGEN_3_8 | SG | 138 | 904 | 120 | 120 | 42500 DOW____POI_5 345 3WXFMR AT3 3 | 7836 | 109 | 112.5 | 85.06 | 93.73 | 2 | 1 | 102.1 | 102 | 26.1 | 24.6 | 0.9667 | 0.9332 | 0.9665 | 0.933 | 0.02 | 0.02
110127 DOWGEN_2_8 138 110128 DOWGEN_3_8 138 SG | 110127 | DOWGEN_2_8 | 110128 | DOWGEN_3_8 | SG | 138 | 904 | 120 | 120 | 42500 DOW____POI_5 345 3WXFMR AT4 4 | 7837 | 109 | 112.5 | 85.06 | 93.72 | 3 | 1 | 102.1 | 102 | 26.1 | 24.6 | 0.9667 | 0.9332 | 0.9665 | 0.9331 | 0.02 | 0.02
110127 DOWGEN_2_8 138 110128 DOWGEN_3_8 138 SG | 110127 | DOWGEN_2_8 | 110128 | DOWGEN_3_8 | SG | 138 | 904 | 120 | 120 | 42500 DOW____POI_5 345 3WXFMR AT5 5 | 7838 | 109 | 112.3 | 85.06 | 93.54 | 4 | 1 | 102.1 | 102 | 26.1 | 24.7 | 0.9667 | 0.9353 | 0.9665 | 0.9351 | 0.02 | 0.02

## ACContSumNotCnv
Cont ID | Cont Name | Status | #Itr | #Pms | #Qms | PmaxMism | Bus# | Bus Name | Base kV | VoltMagPU | QmaxMism | Bus# | Bus Name | Base kV | VoltMagPU | OvlSever | #Ovl | Worst | VltSevrInd | VLow | VHi | Drop | Rise