## 2021_SUM1_TRLProp
Sending System | Receiving System | Max Test MW | Monitored Facility | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Areas Name | Zones | Zones Name | DC TrLim | AC TrLim | Status Message AC TrLim | DfaxDC | DfaxAC | Rate Base | Rate Cont | Cont Name | Cont ID | Base Flow MW (No Transfer) | Cont Flow MW (No Transfer) | DC %Loading (No Transfer) | AC %Loading (No Transfer) | AC %Loading at Tested Limit | HeadRoom | Special Message
Spencer 69kV | GAS_DISPATCH | 200 | 902 POES31569 69.0 981 SPNCRINT69 69.0 1 | 902 | POES31569 | 981 | SPNCRINT69 | 1 | 69 | 19 | DENTNTSP | 3 | DENTON | -2.7 | -2.7 | Limit Found OK | 0.99698 | 0.99231 | 115 | 115 | Base Case | 0 | 117.7 | - | 102.32 | 102.35 | 100.04 | -2.7
Spencer 69kV | GAS_DISPATCH | 200 | 902 POES31569 69.0 981 SPNCRINT69 69.0 1 | 902 | POES31569 | 981 | SPNCRINT69 | 1 | 69 | 19 | DENTNTSP | 3 | DENTON | -2.7 | -2.7 | Limit Found OK | 0.99698 | 0.99233 | 115 | 115 | 904 POLESPL269 69.0 908 SPNCR_SW69 69.0 BC | 649 | 117.7 | 117.7 | 102.32 | 102.35 | 100.04 | -2.7
Spencer 69kV | GAS_DISPATCH | 200 | 981 SPNCRINT69 69.0 982 DN_STEAM_8 138 1 | 981 | SPNCRINT69 | 982 | DN_STEAM_8 | 1 | 69/138 | 19/12 | DENTNTSP/TMPA_TSP | 3/6 | DENTON/TMPA | 7.8 | 5.3 | Limit Found OK | 0.99698 | 1.0094 | 125 | 130 | Base Case | 0 | 117.2 | - | 93.77 | 95.72 | 100 | 7.8
Spencer 69kV | GAS_DISPATCH | 200 | 981 SPNCRINT69 69.0 982 DN_STEAM_8 138 1 | 981 | SPNCRINT69 | 982 | DN_STEAM_8 | 1 | 69/138 | 19/12 | DENTNTSP/TMPA_TSP | 3/6 | DENTON/TMPA | 12.8 | 10.3 | Limit Found OK | 0.99698 | 1.0105 | 125 | 130 | 904 POLESPL269 69.0 908 SPNCR_SW69 69.0 BC | 649 | 117.2 | 117.2 | 90.16 | 92.04 | 100 | 12.8
Spencer 69kV | GAS_DISPATCH | 200 | 906 COOPERCK 138 923 ARCO138 138 1 | 906 | COOPERCK | 923 | ARCO138 | 1 | 138 | 19 | DENTNTSP | 3 | DENTON | 139.5 | 139.5 | Limit Found OK | 0.24773 | 0.24613 | 218 | 218 | 917 POCKRUS138 138 923 ARCO138 138 1 | 657 | 133.2 | 183.5 | 84.15 | 84.05 | 99.8 | 34.5
Spencer 69kV | GAS_DISPATCH | 200 | 906 COOPERCK 138 923 ARCO138 138 1 | 906 | COOPERCK | 923 | ARCO138 | 1 | 138 | 19 | DENTNTSP | 3 | DENTON | 141.9 | 141.9 | Limit Found OK | 0.20077 | 0.2024 | 218 | 218 | 925 LONGROAD138 138 985 N_DENT_8 138 1 | 674 | 133.2 | 189.5 | 86.93 | 87.26 | 100.44 | 28.5
Spencer 69kV | GAS_DISPATCH | 200 | 906 COOPERCK 138 923 ARCO138 138 1 | 906 | COOPERCK | 923 | ARCO138 | 1 | 138 | 19 | DENTNTSP | 3 | DENTON | 142.9 | 142.9 | Limit Found OK | 0.20077 | 0.20217 | 218 | 218 | 923 ARCO138 138 925 LONGROAD138 138 1 | 669 | 133.2 | 189.3 | 86.84 | 87.24 | 100.49 | 28.7

## 2022_HWLL_TRLProp
Sending System | Receiving System | Max Test MW | Monitored Facility | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Areas Name | Zones | Zones Name | DC TrLim | AC TrLim | Status Message AC TrLim | DfaxDC | DfaxAC | Rate Base | Rate Cont | Cont Name | Cont ID | Base Flow MW (No Transfer) | Cont Flow MW (No Transfer) | DC %Loading (No Transfer) | AC %Loading (No Transfer) | AC %Loading at Tested Limit | HeadRoom | Special Message
bakersfield | GAS_DISPATCH | 200 | 7046 L_KENDAL5_1Y 345 7770 L_BERGHE5_1Y 345 1 | 7046 | L_KENDAL5_1Y | 7770 | L_BERGHE5_1Y | 1 | 345 | 7 | LCRA TSC | 130/46 | KENDALL/COMAL | -317.9 | -377.1 | Limit Found OK | 0.14687 | 0.16101 | 1099 | 1099 | 5056 CAGNON_5 345 7046 L_KENDAL5_1Y 345 1 | 3328 | 750.4 | 1145.7 | 104.25 | 105.54 | 100 | -46.7
bakersfield | GAS_DISPATCH | 200 | 7046 L_KENDAL5_1Y 345 5056 CAGNON_5 345 1 | 7046 | L_KENDAL5_1Y | 5056 | CAGNON_5 | 1 | 345 | 5/7 | CPS_TSP/LCRA TSC | 15/130 | BEXAR/KENDALL | -10 | -134 | Limit Found OK | 0.1382 | 0.15133 | 1183 | 1195 | 7046 L_KENDAL5_1Y 345 7770 L_BERGHE5_1Y 345 1 | 4404 | 869.9 | 1196.4 | 100.12 | 101.72 | 100.02 | -1.4