## Slide 1
Screening Study Process
Mario Hayden
Planning Engineer, Resource Integration
10/29/2018

## Slide 2: Study Base Cases
Latest Steady State Working Group (SSWG) cases used
  Summer Peak (SUM1) case used for most Points of Interconnection (POIs)
  SUM1 case year based on COD
  High Wind Low Load (HWLL) case used for POIs electrically close to wind generation
  HWLL case year is same for all studies in same SSWG cycle
Off-cycle updates on MIS are applied to the appropriate study cases as they are released

## Slide 3: Additional Generation
Generation projects that meet Planning Guide Section 6.9(1) after the cut-off date for inclusion in the SSWG base cases are added soon after meeting their requirements
  Projects are added as simple models and are offline by default
  In order for a PG 6.9(1) project to be switched online:
    The COD must fall on or before the study project’s COD
    The PG 6.9(1) project must be in the electrical vicinity of the study project
Projects under study and owned by the Interconnecting Entity (IE) may be added if they share the same POI as the study project

## Slide 4: Generation Dispatch
Generation located in the vicinity of the project are dispatched at a high level, based on technology
Generators at the same POI as the study project are dispatched at 100%, regardless of technology
Changes to online generation and generation dispatch are reported in an appendix of the screening study

## Slide 5: Contingency Analysis
AC Contingency analysis is performed for all P1 and P7 contingencies posted on MIS by the SSWG
Single-element contingencies are also auto-inserted for elements 69kV and higher
Monitored elements with MVA loadings 90% or higher are reported in an appendix
Monitored elements with MVA loadings 100% or higher in the base cases (N-0) are reported in the body of the screening study
Any contingencies that do not converge in the case after case conditioning are also reported in the appendix

## Slide 6: Transfer Analysis Subsystems
During transfer analysis, the study generator is set as a subsystem and a separate subsystem is created with all the online gas units in the case
In scenarios where the study project is a generator or storage in discharging mode, the study gen is set as the sending subsystem and the set of remote, online gas units are set as the receiving subsystem
In scenarios where the study project is storage in charging mode, the study gen is set as the receiving subsystem and all online gas units are set as the sending subsystem

## Slide 7: Transfer Analysis Reporting
Each monitored element/contingency pair violation is reported in an appendix of the screening study where the following are true:
  The generator is dispatched at less than 120% of Pmax
  The generator has a positive shift factor with respect to the constraint
  The generator has a shift factor equal to or greater than 3% with respect to the constraint
The most limiting constraint in each study case is reported in the body of the screening study with the study generator’s MW output (or load if storage), monitored element, and contingency