## Summary
Release Date: November 1, 2018
PRELIMINARY
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Spring 2019
SUMMARY
The ERCOT Region is expected to have sufficient installed generating capacity to serve forecasted peak demands in the upcoming spring season (March - May 2019). ERCOT's scenario analysis also indicates that there will be sufficient capacity even if there is a combination of extreme peak loads and outages.
This preliminary SARA report reflects a spring 2019 peak forecast of 61,566 MW based on current expectations for average weather. A total of 2,262 MW of new nameplate capacity is also expected to be available at the start of the spring season. This capacity total translates into 1,139 MW expected to be available during spring peak load hours, with wind contributing 638 MW, gas-fired units contributing 326 MW, and solar contributing 175 MW.
The report also includes a forecast of 10,564 MW of unit outages based on historical outage data from the past three spring seasons (starting with 2016), and assumes the high likelihood that the spring peak will occur in May. While a significant amount of unit maintenance is conducted during the spring season, much of this maintenance is completed prior to the onset of hotter temperatures (and resulting higher electricity demand) in late May. ERCOT thus assumes for the most extreme scenario that an extreme April peak demand coincides with average April outage amounts occurring during the peak hours of each weekday.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2019 - Preliminary
Release Date: November 1, 2018
Forecasted Capacity and Demand
| Operational Resources (thermal and hydro), MW | 66102.2 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
| Switchable Capacity Total, MW | 3736 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
| less Switchable Capacity Unavailable to ERCOT, MW | -858 | Based on survey responses of Switchable Resource owners
| Available Mothball Resources, MW | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
| Private Use Network Capacity Contribution, MW | 3025.0042 | Average capability of the top 20 hours in the spring peak seasons for the past three years (2015-2018)
| Non-Coastal Wind Resources Capacity Contribution, MW | 5676.18 | Based on 30% of installed capacity for non-coastal wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Coastal Wind Resources Capacity Contribution, MW | 1781.328 | Based on 68% of installed capacity for coastal wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Solar Utility-Scale, Peak Average Capacity Contribution, MW | 965.51 | Based on 65% of rated capacity for solar resources (spring season) per Nodal Protocols Section 3.2.6.2.2
| RMR Resources to be under Contract, MW | 0
| Capacity Pending Retirement, MW | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2
| Non-Synchronous Ties Capacity Contribution, MW | 260.5 | Average net flows for the top 20 hours in the spring peak seasons for the past three years (2015-2018)
| Planned Thermal Resources with Signed IA, Air Permits and Adeq. Water Supplies, MW | 326 | Based on in-service dates provided by developers of generation resources
| Planned Non-Coastal Wind with signed IA , MW | 390.87 | Based on in-service dates provided by developers and 30% spring capacity contribution for non-coastal wind resources
| Planned Coastal Wind with signed IA , MW | 247.452 | Based on in-service dates provided by developers and 68% spring capacity contribution for coastal wind resources
| Planned Solar Utility-Scale with signed IA, MW | 175.11 | Based on in-service dates provided by developers and a spring capacity contribution of 65% for solar resources
[a] Total Resources, MW |  | 81828.1542
[b] Peak Demand, MW |  | 61566 | May peak forecast is based on average weather conditions at time of peak from 2002 – 2016
[c] Reserve Capacity [a - b], MW |  | 20262.1542
Range of Potential Risks
|  | Forecasted Season Peak Load (May) | Extreme Generation Outages During Peak Maintenance Season (March-April) | Extreme Generation Outages During Peak Maintenance Season (March-April) and Extreme Peak Load (April)
| Seasonal Load Adjustment | 0 | -7860 | -779 | April peak forecast is 53,706 MW, and the extreme peak forecast is 60,787 MW; adjustments reflect April peak forecast for average and 90th percentile weather conditions.
| Typical May Maintenance Outages, Thermal | 6024.3118 | 6024.3118 | 6024.3118 | Based on historical average of planned maintenance outages for May weekdays
| Typical May Forced Outages, Thermal | 4539.7618 | 4539.7618 | 4539.7618 | Based on historical average of forced outages for May weekdays
| Incremental Unit Outages to Reflect April Peak Maintenance Season, Thermal | 0 | 7888.0813 | 7888.0813 | Incremental outages based on historical average of forced and planned maintenance outages for April weekdays, hours ending 3 pm - 8 pm (starting with spring 2016)
[d] Total Uses of Reserve Capacity |  | 10564.0735 | 10592.1548 | 17673.1548
[e] Capacity Available for Operating Reserves (c-d), MW |  | 9698.0807 | 9669.9993 | 2588.9993
Less than 2,300 MW indicates risk of EEA1

## Capacities
Unit Capacities - Spring
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | START YEAR | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1227
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1214
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1310
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1310
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 608
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 608
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 448
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785
14 | J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 0
15 | J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 0
16 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824
17 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836
18 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
19 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
20 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
21 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840
22 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825
23 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
24 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
25 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 945
26 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155
27 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155
28 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 664
29 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 663
30 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
31 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
32 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 157
33 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 157
34 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 160
35 | BARNEY M DAVIS REPOWER CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 161
36 | BARNEY M DAVIS REPOWER CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 161
37 | BARNEY M DAVIS REPOWER STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 322
38 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 157
39 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 157
40 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 236
41 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 161.8
42 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 83.6
43 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 161.8
44 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 160.6
45 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 222.4
46 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 169
47 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 169
48 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270
49 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77
50 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77
51 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 71
52 | CALHOUN (PORT COMFORT) 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS | COASTAL | 2017 | 46.7
53 | CALHOUN (PORT COMFORT) 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS | COASTAL | 2017 | 46.7
54 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 168
55 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 168
56 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 182
57 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 74
58 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 67
59 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 100
60 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 73
61 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 68
62 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 105
63 | COLORADO BEND II CT7 |  | CBECII_CT7 | WHARTON | GAS | SOUTH | 2017 | 347.8
64 | COLORADO BEND II CT8 |  | CBECII_CT8 | WHARTON | GAS | SOUTH | 2017 | 346.8
65 | COLORADO BEND II ST8 |  | CBECII_STG9 | WHARTON | GAS | SOUTH | 2017 | 433.4
66 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 181
67 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 178
68 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 178
69 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 144
70 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 190
71 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 202
72 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 190
73 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 202
74 | DEER PARK ENERGY CENTER STG |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290
75 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 174
76 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 209
77 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 116
78 | FERGUSON REPLACEMENT CTG1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 176
79 | FERGUSON REPLACEMENT CTG2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 176
80 | FERGUSON REPLACEMENT STG |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 189
81 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 167
82 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 159
83 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 159
84 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 167
85 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 159
86 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 159
87 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 408
88 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 408
89 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 156.2
90 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 156.2
91 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 178
92 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 156.5
93 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 156.5
94 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 177.1
95 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS | COASTAL | 2000 | 152
96 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS | COASTAL | 2000 | 151
97 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS | COASTAL | 2000 | 75
98 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 158
99 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 158
100 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 158
101 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 158
102 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 200
103 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 200
104 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 213
105 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 214
106 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 213
107 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 216
108 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 143
109 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 143
110 | HIDALGO ENERGY CENTER STG |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 172
111 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2006 | 150
112 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2006 | 150
113 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2006 | 285
114 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 150
115 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 150
116 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 285
117 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163
118 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
119 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 161
120 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 153
121 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 153
122 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 161
123 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
124 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
125 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 183
126 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 175
127 | LOST PINES POWER STG |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 192
128 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 213.6
129 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 213.6
130 | MAGIC VALLEY STATION STG |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 255.5
131 | MIDLOTHIAN ENERGY FACILITY CS 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 232
132 | MIDLOTHIAN ENERGY FACILITY CS 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 230
133 | MIDLOTHIAN ENERGY FACILITY CS 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 229
134 | MIDLOTHIAN ENERGY FACILITY CS 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 232
135 | MIDLOTHIAN ENERGY FACILITY CS 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 244
136 | MIDLOTHIAN ENERGY FACILITY CS 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 246
137 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 161
138 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 161
139 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 322
140 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 156.3
141 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 149.9
142 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 152.4
143 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 150.7
144 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 207.2
145 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 207.2
146 | PANDA SHERMAN POWER CTG1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 218.5
147 | PANDA SHERMAN POWER CTG2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 218.5
148 | PANDA SHERMAN POWER STG |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 353.1
149 | PANDA TEMPLE I POWER CTG1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5
150 | PANDA TEMPLE I POWER CTG2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5
151 | PANDA TEMPLE I POWER STG |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 353.1
152 | PANDA TEMPLE II POWER CTG1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 218.5
153 | PANDA TEMPLE II POWER CTG2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 218.5
154 | PANDA TEMPLE II POWER STG |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 353.1
155 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 86
156 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 86
157 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87
158 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 170
159 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 170
160 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 168
161 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 80
162 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 80
163 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
164 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 80
165 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 80
166 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
167 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 162
168 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 162
169 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 162
170 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323
171 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
172 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51
173 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
174 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
175 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 160
176 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 150
177 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 20
178 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 40
179 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 56
180 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 56
181 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 56
182 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 56
183 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 109
184 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 56
185 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 56
186 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 56
187 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 56
188 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 109
189 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 100.6
190 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 100.6
191 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 100.6
192 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.5
193 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 171
194 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 132
195 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
196 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
197 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
198 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17
199 | WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 211
200 | WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 206
201 | WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 273
202 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 227
203 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 227
204 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 286
205 | WOLF HOLLOW 2 CT5 |  | WHCCS2_CT4 | HOOD | GAS | NORTH | 2017 | 309.1
206 | WOLF HOLLOW 2 CT6 |  | WHCCS2_CT5 | HOOD | GAS | NORTH | 2017 | 309.1
207 | WOLF HOLLOW 2 STG6 |  | WHCCS2_STG6 | HOOD | GAS | NORTH | 2017 | 459
208 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 19
209 | CASTLEMAN CHAMON 1 |  | CHAMON_CTG_0101 | HARRIS | GAS | HOUSTON | 2017 | 46.7
210 | CASTLEMAN CHAMON 2 |  | CHAMON_CTG_0301 | HARRIS | GAS | HOUSTON | 2017 | 46.7
211 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 46.5
212 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 48.5
213 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 50
214 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 50
215 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 50
216 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 50
217 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 71
218 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 70
219 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 70
220 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 71
221 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 153.6
222 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 153.6
223 | ELK STATION CTG 3 |  | AEEC_ELK_3 | HALE | GAS | PANHANDLE | 2016 | 195
224 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 42
225 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 42
226 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 42
227 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 42
228 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 57
229 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 57
230 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 57
231 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 50
232 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 57
233 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 57
234 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.2
235 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.2
236 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.2
237 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 92.9
238 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 90.1
239 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 46
240 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46
241 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 44
242 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46
243 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 67
244 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 66
245 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 66
246 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 67
247 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 68
248 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 68
249 | DENTON ENERGY CENTER A |  | DEC_AGR_A | DENTON | GAS | NORTH | 2018 | 56.5
250 | DENTON ENERGY CENTER B |  | DEC_AGR_B | DENTON | GAS | NORTH | 2018 | 56.5
251 | DENTON ENERGY CENTER C |  | DEC_AGR_C | DENTON | GAS | NORTH | 2018 | 56.5
252 | DENTON ENERGY CENTER D |  | DEC_AGR_D | DENTON | GAS | NORTH | 2018 | 56.5
253 | PEARSALL IC ENGINE PLANT A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
254 | PEARSALL IC ENGINE PLANT B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
255 | PEARSALL IC ENGINE PLANT C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
256 | PEARSALL IC ENGINE PLANT D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
257 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 64
258 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 64
259 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 64
260 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 64
261 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 65
262 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS | HOUSTON | 2018 | 61
263 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS | HOUSTON | 2018 | 62
264 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS | HOUSTON | 2018 | 52
265 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS | HOUSTON | 2018 | 56
266 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS | HOUSTON | 2018 | 56
267 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS | HOUSTON | 2018 | 54
268 | REDGATE A |  | REDGATE_AGR_A | HIDALGO | GAS | SOUTH | 2016 | 56.3
269 | REDGATE B |  | REDGATE_AGR_B | HIDALGO | GAS | SOUTH | 2016 | 56.3
270 | REDGATE C |  | REDGATE_AGR_C | HIDALGO | GAS | SOUTH | 2016 | 56.3
271 | REDGATE D |  | REDGATE_AGR_D | HIDALGO | GAS | SOUTH | 2016 | 56.3
272 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 104
273 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 104
274 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75
275 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5
276 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5
277 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81
278 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81
279 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47
280 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47
281 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47
282 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47
283 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47
284 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47
285 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
286 | SKY GLOBAL POWER ONE A |  | SKY1_SKY1A | COLORADO | GAS | SOUTH | 2016 | 26.7
287 | SKY GLOBAL POWER ONE B |  | SKY1_SKY1B | COLORADO | GAS | SOUTH | 2016 | 26.7
288 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57
289 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57
290 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57
291 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57
292 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57
293 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57
294 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
295 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 89
296 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
297 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
298 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
299 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47
300 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
301 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44
302 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44
303 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44
304 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44
305 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 330
306 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
307 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
308 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 108.5
309 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320
310 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 428
311 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234
312 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
313 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
314 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
315 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
316 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
317 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523
318 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
319 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
320 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
321 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
322 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410
323 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 17.5
324 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 23.5
325 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 39.5
326 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 75
327 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 120
328 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208
329 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
330 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
331 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
332 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
333 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 133
334 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336
335 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
336 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
337 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235
338 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 217
339 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
340 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
341 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
342 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
343 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 246
344 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 536
345 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
346 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
347 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
348 | FORT WORTH METHANE LFG |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6
349 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
350 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2
351 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
352 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
353 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2
354 | VIRIDIS ENERGY-ALVIN LFG |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7
355 | VIRIDIS ENERGY-HUMBLE LFG |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10
356 | VIRIDIS ENERGY-LIBERTY LFG |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9
357 | VIRIDIS ENERGY-TRINITY BAY LFG |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9
358 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
359 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
360 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
361 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
362 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
363 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2
364 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30
365 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9
366 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7
367 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9
368 | OCI ALAMO 1 |  | DG_OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1
369 | TOS BATTERY STORAGE |  | DG_TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2
370 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass less Battery Energy Storage) | [6 empty] | 66016.2
371
372 | Operational Resources (Hydro)
373 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
374 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
375 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
376 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
377 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
378 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
379 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
380 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
381 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
382 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
383 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
384 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
385 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
386 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
387 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
388 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
389 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
390 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
391 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
392 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29
393 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 24
394 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 24
395 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
396 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
397 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
398 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
399 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
400 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
401 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
402 | Operational Capacity Total (Hydro) | [6 empty] | 555.1
403 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 464
404
405 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -378
406 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 66102.2
407
408 | Operational Resources (Switchable)
409 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS | PANHANDLE | 2016 | 56
410 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS | PANHANDLE | 2016 | 56
411 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS | PANHANDLE | 2016 | 56
412 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS | PANHANDLE | 2016 | 195
413 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS | PANHANDLE | 2016 | 195
414 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 178
415 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 180
416 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 307
417 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 178
418 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 180
419 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 307
420 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 180
421 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 180
422 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 180
423 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
424 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162
425 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179
426 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178
427 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389
428 | Switchable Capacity Total | [6 empty] | 3736
429
430 | Switchable Capacity Unavailable to ERCOT
431 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -56
432 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -56
433 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -56
434 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -195
435 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -195
436 | TENASKA FRONTIER STATION |  | FTR_FTR_UNAVAIL | FANNIN | GAS | NORTH | 2016 | -300
437 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  |  |  |  | -858
438
439 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 0
440
441 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 3176.0042
442 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | -151
443
444 | Operational Resources (Wind)
445 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8
446 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120
447 | BLUE SUMMIT WIND 5 |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9
448 | BLUE SUMMIT WIND 6 |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4
449 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2013 | 150
450 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND | PANHANDLE | 2015 | 149.8
451 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND | NORTH | 2017 | 44.9
452 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND | NORTH | 2017 | 55.7
453 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6
454 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5
455 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117
456 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2
457 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88
458 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90
459 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114
460 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5
461 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120
462 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5
463 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5
464 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186
465 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5
466 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75
467 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75
468 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5
469 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD COUNTY | WIND | PANHANDLE | 2017 | 50.4
470 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND | WEST | 2017 | 126.5
471 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND | WEST | 2017 | 126.5
472 | DESERT SKY WIND 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84
473 | DESERT SKY WIND 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5
474 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND | PANHANDLE | 2016 | 100.2
475 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND | PANHANDLE | 2016 | 100.2
476 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7
477 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND | WEST | 2017 | 98.9
478 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND | WEST | 2017 | 131.1
479 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND | PANHANDLE | 2017 | 163.2
480 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND | NORTH | 2018 | 200
481 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND | WEST | 2017 | 79.8
482 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND | WEST | 2017 | 75.6
483 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2
484 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80
485 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6
486 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6
487 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4
488 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8
489 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99
490 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61
491 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND | WEST | 2015 | 150
492 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND | WEST | 2015 | 150
493 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND | WEST | 2016 | 119.9
494 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5
495 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND | PANHANDLE | 2015 | 99.9
496 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND | PANHANDLE | 2015 | 100
497 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REGAN AND IRION | WIND | WEST | 2018 | 152.5
498 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REGAN AND IRION | WIND | WEST | 2018 | 147.5
499 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND | SOUTH | 2016 | 52
500 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND | SOUTH | 2016 | 98
501 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND | SOUTH | 2016 | 100
502 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND | WEST | 2017 | 131.1
503 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND | WEST | 2017 | 98.9
504 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6
505 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158
506 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5
507 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115
508 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 95
509 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND | WEST | 2008 | 102
510 | INDIAN MESA WIND |  | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5
511 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND | SOUTH | 2015 | 19.7
512 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND | SOUTH | 2015 | 230
513 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND | SOUTH | 2017 | 96
514 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND | SOUTH | 2017 | 74
515 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND | SOUTH | 2017 | 30
516 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2
517 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6
518 | KEECHI WIND 138 KV JOPLIN |  | KEECHI_U1 | JACK | WIND | NORTH | 2015 | 110
519 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3
520 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3
521 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3
522 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3
523 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155
524 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND | NORTH | 2015 | 106.3
525 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND | NORTH | 2015 | 103.8
526 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200
527 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100
528 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100
529 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND | PANHANDLE | 2015 | 100
530 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND | PANHANDLE | 2015 | 100
531 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2010 | 49.5
532 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2010 | 51
533 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5
534 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24
535 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND | SOUTH | 2015 | 200
536 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND | SOUTH | 2016 | 200
537 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND | SOUTH | 2016 | 110
538 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND | PANHANDLE | 2017 | 115.2
539 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND | PANHANDLE | 2017 | 115.2
540 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6
541 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6
542 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3
543 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3
544 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150
545 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND | WEST | 2018 | 196.6
546 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6
547 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60
548 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8
549 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD COUNTY | WIND | PANHANDLE | 2017 | 151.2
550 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2
551 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2
552 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2
553 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6
554 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5
555 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5
556 | PANTHER CREEK WIND 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5
557 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5
558 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2
559 | PYRON WIND 1 |  | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 121.5
560 | PYRON WIND 2 |  | PYR_PYRON2 | SCURRY AND FISHER | WIND | WEST | 2008 | 127.5
561 | RATTLESNAKE DEN WIND PHASE 1 G1 |  | RSNAKE_G1 | GLASSCOCK | WIND | WEST | 2015 | 104.3
562 | RATTLESNAKE DEN WIND PHASE 1 G2 |  | RSNAKE_G2 | GLASSCOCK | WIND | WEST | 2015 | 103
563 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84
564 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND | WEST | 2017 | 121.9
565 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND | WEST | 2017 | 27.4
566 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 114
567 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND | WEST | 2008 | 95
568 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND | PANHANDLE | 2015 | 150
569 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND | SOUTH | 2018 | 160
570 | SALT FORK 1 WIND 1 |  | SALTFORK_UNIT1 | DONLEY | WIND | PANHANDLE | 2017 | 64
571 | SALT FORK 1 WIND 2 |  | SALTFORK_UNIT2 | DONLEY | WIND | PANHANDLE | 2017 | 110
572 | SAND BLUFF WIND |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90
573 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND | SOUTH | 2015 | 76
574 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150
575 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND | WEST | 2015 | 204.1
576 | SHERBINO 1 WIND |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150
577 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 145
578 | SILVER STAR WIND |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60
579 | SNYDER WIND |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63
580 | SOUTH PLAINS WIND I |  | SPLAIN1_WIND1 | FLOYD | WIND | PANHANDLE | 2015 | 102
581 | SOUTH PLAINS WIND 2 |  | SPLAIN1_WIND2 | FLOYD | WIND | PANHANDLE | 2015 | 98
582 | SOUTH PLAINS WIND II A |  | SPLAIN2_WIND21 | FLOYD | WIND | PANHANDLE | 2016 | 148.5
583 | SOUTH PLAINS WIND II B |  | SPLAIN2_WIND22 | FLOYD | WIND | PANHANDLE | 2016 | 151.8
584 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2
585 | SPINNING SPUR WIND TWO |  | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161
586 | SPINNING SPUR 3 [WIND 1] |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND | PANHANDLE | 2015 | 96
587 | SPINNING SPUR 3 [WIND 2] |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND | PANHANDLE | 2015 | 98
588 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120
589 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2
590 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND | WEST | 2015 | 164.7
591 | SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 42.5
592 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 16.8
593 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 103.8
594 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 34
595 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 117
596 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 85
597 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 112
598 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 125
599 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7
600 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6
601 | TRENT WIND |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150
602 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5
603 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5
604 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5
605 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND | NORTH | 2017 | 125.6
606 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND | PANHANDLE | 2016 | 114.9
607 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND | PANHANDLE | 2016 | 142.3
608 | WEST TEXAS WIND |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3
609 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57
610 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 92.3
611 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6
612 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30
613 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND | WEST | 2017 | 125
614 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND | WEST | 2017 | 125
615 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5
616 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2
617 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | 1
618 | Operational Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 18920.6
619 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 30
620
621 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
622 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
623 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120
624 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108
625 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
626 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6
627 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4
628 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
629 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
630 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
631 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6
632 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
633 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
634 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
635 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
636 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
637 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
638 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
639 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2
640 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
641 | Operational Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 2619.6
642 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 68
643
644 | Operational Wind Capacity Total (All Counties) |  | WIND_OPERATIONAL |  |  |  |  | 21540.2
645
646 | Operational Resources (Solar)
647 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
648 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1
649 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6
650 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180
651 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22
652 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1
653 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
654 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
655 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95
656 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2
657 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 106.4
658 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
659 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
660 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150
661 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50
662 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5
663 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
664 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
665 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
666 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
667 | FIFTH GENERATION SOLAR 1 |  | DG_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
668 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
669 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
670 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
671 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2
672 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
673 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
674 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
675 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
676 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10
677 | Operational Capacity Total (Solar) | [6 empty] | 1485.4
678 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 65
679
680 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0
681
682 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0
683
684 | Non-Synchronous Tie Resources
685 | EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600
686 | NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220
687 | EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30
688 | LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100
689 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150
690 | SHARYLAND RAILROAD TIE 2 |  | DC_R2 | HIDALGO |  | SOUTH |  | 150
691 | Non-Synchronous Ties Total | [6 empty] | 1250
692 | Non-Synchronous Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 260.5
693
694 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
695 | FGE TEXAS I PROJECT | 16INR0010 |  | MITCHELL | GAS | WEST | 2021 | 0
696 | FRIENDSWOOD G | 13INR0049 |  | HARRIS | GAS | HOUSTON | 2018 | 119
697 | HALYARD HENDERSON | 16INR0045 |  | HENDERSON | GAS | NORTH | 2021 | 0
698 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS | SOUTH | 2020 | 0
699 | HUDSON (BRAZORIA ENERGY G) | 16INR0076 |  | BRAZORIA | GAS | COASTAL | 2019 | 96
700 | MIRAGE | 17INR0022 |  | HARRIS | GAS | HOUSTON | 2019 | 11
701 | VICTORIA CITY (CITYVICT) | 18INR0035 |  | VICTORIA | GAS | SOUTH | 2019 | 0
702 | VICTORIA PORT (VICTPORT) | 17INR0045 |  | VICTORIA | GAS | SOUTH | 2018 | 100
703 | Planned Capacity Total (Coal, Gas & Storage) | [6 empty] | 326
704
705 | Planned Wind Resources with Executed SGIA
706 | ARMSTRONG WIND | 18INR0029 |  | ARMSTRONG | WIND | PANHANDLE | 2020 | 0
707 | BARROW RANCH (JUMBO HILL WIND) | 18INR0038 |  | ANDREWS | WIND | WEST | 2019 | 0
708 | BLUE SUMMIT II | 18INR0070 |  | WILBARGER | WIND | WEST | 2019 | 102
709 | CABEZON WIND (RIO BRAVO I WIND) | 17INR0005 |  | STARR | WIND | SOUTH | 2019 | 0
710 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND | WEST | 2018 | 148.4
711 | CANADIAN BREAKS WIND | 13INR0026 |  | OLDHAM | WIND | PANHANDLE | 2019 | 0
712 | CANYON WIND | 18INR0030 |  | SCURRY | WIND | WEST | 2020 | 0
713 | COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2019 | 0
714 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND | WEST | 2019 | 0
715 | DARMSTADT | 18INR0023 |  | SCHLEICHER | WIND | WEST | 2019 | 0
716 | EASTER WIND | 15INR0063 |  | CASTRO | WIND | PANHANDLE | 2020 | 0
717 | EDMONDSON RANCH WIND | 18INR0043 |  | GLASSCOCK | WIND | WEST | 2020 | 0
718 | FOARD CITY WIND | 19INR0019 |  | FOARD | WIND | WEST | 2019 | 0
719 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND | PANHANDLE | 2019 | 0
720 | GOPHER CREEK WIND | 18INR0067 |  | SCURRY | WIND | WEST | 2019 | 0
721 | HARALD (BEARKAT WIND B) | 15INR0064b |  | GLASSCOCK | WIND | WEST | 2019 | 0
722 | HART WIND | 16INR0033 |  | CASTRO | WIND | PANHANDLE | 2020 | 0
723 | HIGH LONESOME W | 19INR0038 |  | CROCKETT | WIND | WEST | 2019 | 0
724 | KONTIKI 1 WIND | 19INR0099a |  | GLASSCOCK | WIND | WEST | 2019 | 0
725 | KONTIKI 2 WIND | 19INR0099b |  | GLASSCOCK | WIND | WEST | 2020 | 0
726 | LOCKETT WIND FARM | 16INR0062b |  | WILBARGER | WIND | WEST | 2019 | 0
727 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND | SOUTH | 2019 | 0
728 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND | WEST | 2018 | 100
729 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2018 | 152.5
730 | MAVERICK CREEK I | 20INR0045 |  | CONCHO | WIND | WEST | 2020 | 0
731 | MAVERICK CREEK II | 20INR0046 |  | CONCHO | WIND | WEST | 2020 | 0
732 | MESTENO WIND | 16INR0081 |  | STARR | WIND | SOUTH | 2019 | 0
733 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND | PANHANDLE | 2019 | 0
734 | OVEJA WIND | 18INR0033 |  | IRION | WIND | WEST | 2019 | 0
735 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2020 | 0
736 | PRAIRIE HILL WIND | 19INR0100 |  | LIMESTONE | WIND | NORTH | 2020 | 0
737 | PUMPKIN FARM WIND | 16INR0037c |  | FLOYD | WIND | PANHANDLE | 2019 | 0
738 | RANCHERO WIND | 20INR0011 |  | CROCKETT | WIND | WEST | 2019 | 0
739 | RTS 2 WIND (HEART OF TEXAS WIND) | 18INR0016 |  | MCCULLOCH | WIND | SOUTH | 2019 | 0
740 | S_HILLS WIND (LITTLE MOUNTAIN WIND) | 12INR0055 |  | BAYLOR | WIND | WEST | 2019 | 0
741 | SAGE DRAW WIND | 19INR0163 |  | LYNN | WIND | WEST | 2019 | 0
742 | SCANDIA WIND DEF | 13INR0010def |  | PARMER | WIND | PANHANDLE | 2019 | 0
743 | SILVER CANYON WIND A | 12INR0002a |  | BRISCOE | WIND | PANHANDLE | 2020 | 0
744 | TAHOKA WIND (STAKED PLAINS WIND 1) | 18INR0025 |  | LYNN | WIND | WEST | 2019 | 300
745 | TG EAST WIND | 19INR0052 |  | KNOX | WIND | WEST | 2019 | 0
746 | TORRECILLAS WIND | 14INR0045 |  | WEBB | WIND | SOUTH | 2018 | 300.5
747 | VERA WIND | 19INR0051 |  | KNOX | WIND | WEST | 2019 | 0
748 | WILDROSE WIND (SWISHER WIND) | 13INR0038 |  | SWISHER | WIND | PANHANDLE | 2020 | 0
749 | WILSON RANCH (INFINITY LIVE OAK WIND) | 12INR0060 |  | SCHLEICHER | WIND | WEST | 2018 | 199.5
750 | WKN AMADEUS WIND | 14INR0009 |  | KENT | WIND | WEST | 2019 | 0
751 | CHALUPA WIND | 20INR0042 |  | CAMERON | WIND-C | COASTAL | 2020 | 0
752 | CRANEL WIND | 19INR0112 |  | REFUGIO | WIND-C | COASTAL | 2019 | 0
753 | KARANKAWA 2 WIND FARM | 19INR0074 |  | SAN PATRICIO | WIND-C | COASTAL | 2019 | 0
754 | KARANKAWA WIND ALT A | 18INR0014 |  | SAN PATRICIO | WIND-C | COASTAL | 2019 | 0
755 | LAS MAJADAS WIND | 17INR0035 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
756 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | COASTAL | 2018 | 162.9
757 | PALMAS ALTAS WIND | 17INR0037 |  | CAMERON | WIND-C | COASTAL | 2019 | 0
758 | SHAFFER (PATRIOT WIND/PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2019 | 0
759 | PEYTON CREEK WIND | 18INR0018 |  | MATAGORDA | WIND-C | COASTAL | 2019 | 0
760 | RAYMOND WIND | 18INR0059 |  | WILLACY | WIND-C | COASTAL | 2019 | 0
761 | STELLA 1 WIND | 15INR0035 |  | KENEDY | WIND-C | COASTAL | 2018 | 201
762 | Planned Capacity Total (Wind) | [6 empty] | 1666.8
763
764 | Planned Wind Capacity Sub-total (Non-Coastal Counties) |  | WIND_PLANNED_NC |  |  |  |  | 1302.9
765 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PL_PEAK_PCT_NC | % |  |  |  | 30
766
767 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 363.9
768 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 68
769
770 | Planned Solar Resources with Executed SGIA
771 | ARAGORN SOLAR | 19INR0088 |  | CULBERSON | SOLAR | WEST | 2020 | 0
772 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) | 16INR0019 |  | COKE | SOLAR | WEST | 2018 | 30
773 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 |  | PECOS | SOLAR | WEST | 2019 | 0
774 | FS BARILLA SOLAR 1B [HOVEY_UNIT2] | 12INR0059b |  | PECOS | SOLAR | WEST | 2018 | 7.4
775 | LAMESA SOLAR (PHASE II) | 16INR0023b |  | DAWSON | SOLAR | WEST | 2018 | 50
776 | LONG DRAW SOLAR | 18INR0055 |  | BORDEN | SOLAR | WEST | 2020 | 0
777 | MISAE SOLAR | 18INR0045 |  | CHILDRESS | SOLAR | PANHANDLE | 2019 | 0
778 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2020 | 0
779 | OBERON SOLAR | 19INR0083 |  | ECTOR | SOLAR | WEST | 2019 | 0
780 | PFLUGERVILLE SOLAR | 15INR0090 |  | TRAVIS | SOLAR | SOUTH | 2019 | 0
781 | PHOEBE SOLAR | 19INR0029 |  | WINKLER | SOLAR | WEST | 2019 | 0
782 | PROSPERO SOLAR | 19INR0092 |  | ANDREWS | SOLAR | WEST | 2019 | 0
783 | QUEEN SOLAR | 19INR0102 |  | UPTON | SOLAR | WEST | 2019 | 0
784 | RAMBLER SOLAR | 19INR0114 |  | TOM GREEN | SOLAR | WEST | 2019 | 0
785 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2019 | 0
786 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2019 | 0
787 | RE MAPLEWOOD 2C SOLAR | 17INR0020c |  | PECOS | SOLAR | WEST | 2019 | 0
788 | RE MAPLEWOOD 2D SOLAR | 17INR0020d |  | PECOS | SOLAR | WEST | 2020 | 0
789 | RE MAPLEWOOD 2E SOLAR | 17INR0020e |  | PECOS | SOLAR | WEST | 2020 | 0
790 | SODA LAKE SOLAR 1 | 18INR0040 |  | CRANE | SOLAR | WEST | 2020 | 0
791 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2020 | 0
792 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2019 | 0
793 | WAYMARK SOLAR | 16INR0115 |  | PECOS | SOLAR | WEST | 2018 | 182
794 | WEST OF PECOS SOLAR | 14INR0044 |  | REEVES | SOLAR | WEST | 2019 | 0
795 | WINKLER SOLAR (RES WINK SOLAR) | 18INR0022 |  | WINKLER | SOLAR | WEST | 2019 | 0
796 | Planned Capacity Total (Solar) | [6 empty] | 269.4
797 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 65
798
799 | Seasonal Mothballed Resources
800 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 57
801 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
802 | Total Seasonal Mothballed Capacity | [6 empty] | 118
803
804 | Mothballed Resources
805 | GIBBONS CREEK U1 (OCT 2018 TO MID-MAY/JUN 2019) |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470
806 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 420
807 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
808 | S R BERTRON U1 (SINCE 5/15/2013) |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 115
809 | S R BERTRON U2 (SINCE 5/15/2013) |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 171
810 | Total Mothballed Capacity | [6 empty] | 1596
811
812 | Notes:
813 | Capacity changes due to planned repower projects are reflected in the operational units' ratings upon project completion.
814 | Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational capacity formula. These resources
815 | are assumed to be available for less than an hour on a sustained basis.

## Background
Release Date: November 1, 2018
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses an operating reserve threshold of 2,300 MW to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) may be triggered during the time of the forecasted seasonal peak load. This threshold level is intended to be roughly analogous to the 2,300 MW Physical Responsive Capability (PRC) threshold for EEA1. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 MW reserve capacity threshold is a reasonable indicator for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variation in these parameters is based on historic ranges of the parameter values or known changes expected in the near-term. The SARA report is not intended to indicate the likelihood of any of these scenario outcomes.