## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Chad Mulholland, NRG
ROS
November 8th, 2018

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    Two FMEs on the last day of August and 4 FMEs in month of September
  Frequency Control Report
  Regulation Report

## Slide 3: Meeting Minutes
PDCWG Meeting 10/22/18
  SCT DC Tie Directive 9 – MSSC Whitepaper and Ancillary Service Requirements
  Draft NOGRR Realignment with NPRR863
  SCR795-Intra Hour Wind Forecast Accuracy
  Review PDCWG Scope
  Regulation & Frequency Control Reports
  BAL-001-TRE-01 SDT Nominations Submitted for Approval

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 2 FMEs at the end of August
  8/31/2018 12:03:57
    Loss of 527 MW
    Interconnection Frequency Response:
    19 of 59 Evaluated Generation Resources ( 5 of 24 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    15 of 59 Evaluated Generation Resources ( 3 of 24 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.
  8/31/2018 22:33:31
    Loss of 646 MW
    Interconnection Frequency Response:
    9 of 54 Evaluated Generation Resources ( 0 of 23 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    8 of 54 Evaluated Generation Resources ( 0 of 23 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
There were 4 FMEs in the month of September
  9/1/2018 10:38:31
    Loss of 637 MW
    Interconnection Frequency Response:
    11 of 47 Evaluated Generation Resources ( 2 of 27 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    10 of 47 Evaluated Generation Resources ( 3 of 27 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.
  9/4/2018 19:30:21
    Loss of 860 MW
    Interconnection Frequency Response:
    7 of 42 Evaluated Generation Resources ( 6 of 30 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    6 of 42 Evaluated Generation Resources ( 2 of 30 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Frequency Measurable Events
  9/19/2018 20:43:20
    Loss of 769 MW
    Interconnection Frequency Response:
    7 of 43 Evaluated Generation Resources(1 of 26 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    6 of 43 Evaluated Generation Resources(0 of 26 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.
  9/24/2018 01:39:15
    Loss of 653 MW
    Interconnection Frequency Response:
    6 of 61 Evaluated Generation Resources(0 of 27 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    4 of 61 Evaluated Generation Resources(1 of 27 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 8: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 921.60 MW/0.1Hz

## Slide 9: Frequency Control Report
September 2018

## Slide 10: CPS1 Performance

## Slide 11: RMS1 Performance of ERCOT Frequency

## Slide 12: Frequency Profile Analysis

## Slide 13: Time Error Corrections

## Slide 14: ERCOT Total Energy

## Slide 15: ERCOT Total Energy from Wind Generation

## Slide 16: ERCOT % Energy from Wind Generation

## Slide 17
Questions?