## Slide 1
ERCOT Frequency Control Report
October 2018
ERCOT
Operations Planning
PDCWG | November 9th, 2018

## Slide 2: Summary of October 2018
CPS1: 176.03%
Current CPS1 12-Month Rolling Average: 175.98%
1 BAAL Exceedance
5 hourly CPS1 scores below 100%
BAAL-003 Events have updated through August
2018 BAAL-003 FRM Performance: -895.19
2018 RMS1 Statistics
  Mean: 14.55 mHz
  Min: 11.40 mHz
  Max: 19.12 mHz
October Energy Statistics
  Total Energy: 29,156,994 MWh
  Wind Energy: 5,239,561 MWh
  Percent Energy from Wind Generation: 17.97%
October Minimum System Inertia
  Mean: 190,188
  Max: 228,144 on October 9th
  Min: 145,241 on October 30th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
October-18 CPS1 (%): 176.03
Notes: Outliers:
10/6/18 01:00: 0.48%
Wind ramp down of >2,000 MW throughout the hour. Frequency was dragging due to wind ramp and large expected generation deviation. Reg Up exhausted from 01:04 until 01:36. Loss of approx. 500 MW at 01:23 due to unit trip/run back
10/8/18 16:00: 95.47%
Wind ramp down of >1,000 MW throughout the hour. Solar ramp down of 400 MW from 16:42 until the end of the hour. Reg Up exhausted from 16:20.
10/8/18 20:00: 77.58%
Wind ramp down of >1,000 MW throughout the hour. Reg Up exhausted for the majority of the hour.
10/12/18 16:00: 89.58%
Large expected generation deviation, a couple units not following base point during the first 15 min of the hour. Solar ramp down of approx. 200 MW. Wind ramp down of approx. 400 MW. Reg Up exhausted for the majority of the hour
10/15/18 19:00: 82.84%
Wind ramp down of approx. 1,500 MW. Several units lagging behind base points, large expected generation deviation. Reg Up exhausted for the majority of the hour.

## Slide 5: BAAL Exceedances & Violations
There was 1 BAAL exceedance
  October 6, 2018
    Wind was ramping down quickly
    Unit loss when there was already a large expected generation deviation
    Less than 59.91 Hz for 1 minute

## Slide 6: 15-Minute Average CPS1%
October-18 CPS1 (%): 176.03

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 175.98%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 14.68 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 14.55 mHz
Min: 11.40 mHz
Max: 19.12 mHz

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Frequency Profile Comparison

## Slide 15: Time Error Correction

## Slide 16: ERCOT Daily Time Error

## Slide 17: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 18: BAL-003 Performance

## Slide 19: Op. Year 2018 BAL-003 Selected Events
Maybe. Will be valuated at the end of the year.

## Slide 20: Op. Year 2018 BAL-003 FRM Performance

## Slide 21: ERCOT Energy Statistics

## Slide 22: Total Energy
Notes: 29,156,994 MWh

## Slide 23: Total Energy from Wind Generation
Notes: 5,239,561 MWh

## Slide 24: % Energy from Wind Generation
Notes: 17.97%

## Slide 25: ERCOT System Inertia

## Slide 26: Daily Minimum System Inertia
Notes: Minimum Inertia = 130,014 MW*s on 10/27/2017. This was also our record wind day.
October
Mean: 190,188
Max: 228,144 on October 9th
Min: 145,241 on October 30th

## Slide 27: Questions?
Thank you!

## Slide 28: Op. Year 2017 BAL-003 Selected Events
Notes: Frequency Bias updated from 764 to 759 in April

## Slide 29: Op. Year 2017 BAL-003 FRM Performance