## Slide 1
Unannounced Capacity Testing
Summer 2018 Summary
November 8, 2018
ROS
ERCOT Staff

## Slide 2: Background
ERCOT conducts unannounced Generation Resource tests to verify HSL reported by telemetry is achievable.
ERCOT is required to report aggregated results of such unannounced tests to ROS on an annual basis.
8.1.1.2 General Capacity Testing Requirements
To verify that the HSL reported by telemetry is achievable, ERCOT may, at its discretion, conduct an unannounced Generation Resource test….
ERCOT shall maintain historical records of unannounced Generation Resource test results, using the information contained therein to adjust the Reserve Discount Factor (RDF) subject to the approval of the appropriate TAC subcommittee. ERCOT shall report to the Reliability and Operations Subcommittee (ROS) annually or as requested by ROS the aggregated results of such unannounced testing (excluding retests), including, but not limited to, the number and total capacity of Resources tested, the percentage of Resources that met or exceeded their HSL reported by telemetry, the percentage that failed to meet their HSL reported by telemetry, and the total MW capacity shortfall of those Resources that failed to meet their HSL reported by telemetry.

## Slide 3: New Selection Process
We have developed a tool to identify list of Resources using historical information that have not operated close to their HSL.
This approach has allowed ERCOT to more effectively to prepare the list of Generation Resources that may be tested.

## Slide 4: Unannounced Unit Testing Summary - Summer 2018
Unannounced Resource Capacity Testing Summary |  |  |  |  |  |  |  | 
All Tests from Summer 2018 |  |  |  |  |  |  |  | 
Resources Tested: | 35 | resources |  |  |  |  |  | 
Distinct Resources Tested: | 29 | resources |  |  |  |  |  | 
Distinct QSE's Tested: | 20 | resources |  |  |  |  |  | 
Capacity of Resources Tested: | 17,588 | MW |  |  |  |  |  | 
Resources Passed: |  | 17 | resources | Resources Failed: |  | 18 | resources | 
Cap. of Resources Passed: |  | 8,133 | MW |  | Cap. Of Resources Failed: | 9,455 | MW | 
HSL Reached and Sustained: |  | 17 | resources |  |  |  |  | 
HSL Not Reached: |  |  |  |  |  | 10 | resources | 
HSL Not Reached and Not Sustained: |  |  |  |  |  | 2 | resources | 
HSL Reached but Not Sustained: |  |  |  |  |  | 6 | resources | 
Total MW Capacity Excess of Passed Resources: |  |  |  |  | 71 | MW |  | 
Total MW Capacity Shortfall of Failed Resources: |  |  |  |  | 104 | MW |  | 
Total MW Capacity Shortfall of All Resources: |  |  |  |  | 33 | MW |  | 
33 MW NET shortfall of capacity.

## Slide 5: Unannounced Unit Testing Summary - Summer 2018
Chart: Capacity Testing Results by Ambient Temperature for Summer 2018
| T <= 85 | 85 < T <= 95 | 95 > T
Pass | 0 | 10 | 7
Fail | 0 | 13 | 5
Pass Rate | 0 | 0.43478 | 0.58333
Capacity Shortfall (T > 95) | 
Excess | 29 MW
Shortfall | -12 MW
Net | 17 MW

## Slide 6
Further Discussion