## Slide 1
Follow-up to WMS Review of July and August Reliability Unit Commitments for Capacity
Market Analysis
November 12, 2018

## Slide 2: Introduction
ERCOT presented details of the July 26th and August 1st and 2nd RUCs for capacity at the October 10, 2018 WMS meeting
Stakeholders requested ERCOT provide certain additional details, which are contained in this presentation

## Slide 3: July 26th RUC for Capacity
ERCOT was projecting a reserve capacity shortage and issued an OCN at 9:06 AM
10 AM HRUC showed 3,114 MW short for HE 17
  1 Resource committed (36 MW)
  42 Resources deferred
1,669 MW of Resources with start-up times < 1 hour were showed at OFF for HE 17
  Excludes Combined-Cycle Resources
Chart: Forecasted Load vs. Projected Online Capacity during July 26, 2018 HRUC at 10 AM
| 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
HASL-Load | 1376.1 | -589 | -1882.2 | -2711.3 | -3113.5 | -2018.9 | -1599.3 | -1449.6 | -682 | 1949
HSL | 67481 | 69172 | 70646 | 71098 | 71280 | 71704 | 70331 | 68174 | 66091 | 66201
HASL | 64784.1 | 66511 | 68029.8 | 68481.7 | 68651.5 | 69090.1 | 67850.7 | 65646.4 | 63585 | 63710
Load | 63408 | 67100 | 69912 | 71193 | 71765 | 71109 | 69450 | 67096 | 64267 | 61761

## Slide 4: July 26th RT Reserve Capacity vs. 10 AM RUC
Chart: Forecast Error and Additional Capacity in SCED from July 26, 2018 Snapshot at 10 AM
| 15 | 16 | 17 | 18
Additional IRR HSL | -373 | -470.3 | -59.8 | -223.8
DC Tie Error | -161.5044 | -259.3382 | -259.3842 | -262.5726
Additional Off HSL (CST > 1) | 690.8 | 1044.8 | 1499.8 | 1524.3
Additional Off HSL (CST <= 1) | 560.7 | 566.5 | 567 | 567
Additional HSL already Online | 194.5 | 186.4 | 234 | 85.9
Load Forecast Error | 1699.2031 | 1286.0625 | 1077.3984 | 815.7734
RUC HSL | 33.9 | 34 | 35 | 36
Combined Reserve Error to Real-Time | 2644.5987 | 2388.1243 | 3094.0143 | 2542.6008

## Slide 5: August 1st RUC for Capacity
ERCOT was projecting a reserve capacity shortage and issued an OCN at 2:36 AM.
7 AM HRUC showed 4,093 MW short for HE 17
  2 Resources committed (788 MW)
  40 Resources deferred
2,138 MW of Resources with start-up times < 1 hour were showed at OFF for HE 17
  Excludes Combined-Cycle Resources
Chart: Forecasted Load vs. Projected Online Capacity during August 1, 2018 HRUC at 7 AM
| 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
HASL-Load | 2445 | 888.3 | -1284.3 | -2519.7 | -4093.3 | -3772.4 | -2796.5 | -561.8 | 964.9 | 4171.9
HSL | 61023 | 62271 | 62625 | 63874 | 64053 | 64331 | 63333 | 62657 | 61941 | 62038
HASL | 58255 | 59524.3 | 60129.7 | 61361.3 | 61571.7 | 61823.6 | 60834.5 | 60182.2 | 59612.9 | 59692.9
Load | 55810 | 58636 | 61414 | 63881 | 65665 | 65596 | 63631 | 60744 | 58648 | 55521

## Slide 6: August 1st RT Reserve Capacity vs. 7 AM RUC
Chart: Forecast Error and Additional Capacity in SCED from August 1, 2018 Snapshot at 7 AM
| 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Load Forecast Error | -957.1211 | -1089.5391 | -909.9805 | -472.9023 | 104.1641 | 112.1172 | -473.9492 | -801.6172
Additional HSL already Online | -11.3 | -425.1 | -231.3 | 9.2 | 391.6 | -220.1 | -442.2 | -371.2
Additional IRR HSL | -141 | -225.4 | -395.5 | -336.5 | -227.9 | -369.4 | -149.5 | -9.1
DC Tie Difference | 490.2046 | 629.6051 | 635.779 | 629.7117 | 628.4891 | 635.8716 | 632.7726 | 678.7019
Additional Off HSL (CST > 1) | 1104.6 | 1317 | 2454.9 | 2948.9 | 2928.9 | 2942.2 | 3951.9 | 2452.4
Additional Off HSL (CST <= 1) | -269.7 | 393.5 | 517.7 | 585.6 | 105.2 | 595.9 | 601.2 | 753.6
RUC HSL | 0 | 232.9 | 788 | 788 | 788 | 788 | 788 | 395.9
Combined MW Error to Real-Time | 492.9 | 1771.4 | 3741.5 | 4670.8 | 4231 | 4422.5 | 5440.6 | 3865.2

## Slide 7: August 2nd 9 AM RUC for Capacity
ERCOT was projecting a reserve capacity shortage and issued an OCN on 8/1/18 9:59 PM.
9 AM HRUC showed 4,142 MW short for HE 17
  3 Resources committed (972 MW)
  28 Resources deferred
1,842 MW of Resources with start-up times < 1 hour were showed at OFF for HE 17
  Excludes Combined-Cycle Resources
Chart: Forecasted Load vs. Projected Online Capacity during August 2, 2018 HRUC at 9 AM
| 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
HASL-Load | 77 | -1574.1 | -2908.3 | -3313.6 | -4142.3 | -3698.6 | -2365.4 | -466.9 | 1112 | 3870.5
HSL | 61334 | 62664 | 63523 | 65014 | 65374 | 65449 | 64806 | 63872 | 63201 | 62971
HASL | 58563 | 59825.9 | 61024.7 | 62536.4 | 62965.7 | 62979.4 | 62380.6 | 61455.1 | 60855 | 60671.5
Load | 58486 | 61400 | 63933 | 65850 | 67108 | 66678 | 64746 | 61922 | 59743 | 56801

## Slide 8: August 2nd RT Reserve Capacity vs. 9 AM RUC
Chart: Forecast Error and Additional Capacity in SCED from August 2, 2018 Snapshot at 9 AM
| 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
DC Tie Difference | -3.6689 | -3.3975 | -4.2691 | -3.3778 | -4.763 | -7.0074 | -7.3569 | -0.9666
Additional IRR HSL | -472.7 | -304.1 | -353.1 | -383.5 | -570 | -415.9 | -488.2 | -459.9
Additional HSL already Online | 7.2 | -295.4 | 46.5 | 327.4 | 178.1 | -68.5 | -147.1 | 356.7
Load Forecast Error | 656.2695 | 342.4414 | 382.3125 | 495.6875 | 984.4453 | 979.7109 | 519.0625 | 285.8438
Additional Off HSL (CST > 1) | 305.4 | 1084.5 | 2122 | 2175.3 | 2719.2 | 2860.6 | 3001.6 | 1579.4
Additional Off HSL (CST <= 1) | 440.9 | 712.6 | 730.5 | 734.4 | 742.5 | 747.7 | 786.9 | 731.6
RUC HSL | 657.3 | 994.3 | 1474 | 993 | 1209 | 1009.7 | 1175.9 | 567.2
Combined MW Error to Real-Time | 1590.7006 | 2530.9439 | 4397.9434 | 4338.9097 | 5258.4823 | 5106.3035 | 4840.8056 | 3059.8771

## Slide 9: August 2nd 10 AM RUC for Capacity
OCN from 8/1/18 9:59 PM still in effect
10 AM HRUC showed 2,377 MW short for HE 17
  2 Resources committed (739 MW)
  24 Resources deferred
1,898 MW of Resources with start-up times < 1 hour were showed at OFF for HE 17
  Excludes Combined-Cycle Resources
Total of 1,209 MW committed at HE 17 in 9 AM and 10 AM RUCs
Chart: Forecasted Load vs. Projected Online Capacity during August 2, 2018 HRUC at 10 AM
| 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
HASL-Load | 460 | -719.1 | -1190.3 | -1544.6 | -2377.3 | -1638.6 | -1486.4 | 32.1 | 1134 | 3813.5
HSL | 61559 | 63560 | 65260 | 66800 | 67183 | 67536 | 65717 | 64414 | 63278 | 62971
HASL | 58780 | 60722.9 | 62761.7 | 64323.4 | 64721.7 | 65067.4 | 63291.6 | 61998.1 | 60931 | 60671.5
Load | 58320 | 61442 | 63952 | 65868 | 67099 | 66706 | 64778 | 61966 | 59797 | 56858

## Slide 10: August 2nd RT Reserve Capacity vs. 10 AM RUC
Chart: Forecast Error and Additional Capacity in SCED from August 2, 2018 Snapshot at 10 AM
| 15 | 16 | 17 | 18 | 19
DC Tie Difference | -4.2691 | -3.3778 | -4.763 | -7.0074 | -7.3569
Additional IRR HSL | -223.1 | -304.9 | -514.3 | -639.3 | -490.8
Additional Off HSL (CST > 1) | 1380 | 1433.7 | 2039 | 2123.6 | 2787.6
Additional Off HSL (CST <= 1) | 25.7 | 25.7 | 25.7 | 25.7 | 75.7
Additional HSL already Online | 598.3 | 884.7 | 682.1 | 498.5 | 406.1
Load Forecast Error | 400.9062 | 513.8438 | 975.9922 | 1008.0625 | 550.4766
RUC HSL | 502 | 21 | 237 | 37.7 | 638.9
Combined MW Error to Real-Time | 2679.5372 | 2570.666 | 3440.7292 | 3047.2551 | 3960.6196

## Slide 11: NPRR 864 HRUC Re-Runs
HRUC Re-Runs were conducted mimicking the implementation of NPRR 864
Resources with cold start time less than or equal to 1 hour had Start Up and Min Gen costs reduced to 20% of verifiable or generic
HRUC Case | RUC Count (Original→Rerun) | RUC HSL MWh (Original→Rerun) | Committed Resource(s)
7/26 10AM | 43→39 | 8,561→8,572 | Still recommended
8/1 7AM | 42→44 | 17,277→17,111 | Still recommended
8/2 9AM | 31→37 | 15,569→15,335 | Still recommended
8/2 10AM | 26→36 | 5,039→4,661 | No longer recommended. Decisions on alternative recommendations could have been deferred.

## Slide 12: Additional Questions Related to NPRR 864
How much additional capacity was available from online Combined Cycle Resources that could transition to a larger configuration?
  During periods of RUC commitments no additional capacity was available from CCs transitioning to larger configurations

## Slide 13: Additional Questions Related to NPRR 864
Was there capacity with CST >1 that was in a warm or hot state and had a start time <=1 hour?
Capacity from Resources that are:
  Available for RUC recommendation
  Cold start time >1 hour
  Hot or warm state with related startup time <= 1 hour
HRUC Case | Sum of HSL (MW) | Already Recommended?
7/26 10AM | 322 | Yes
8/1 7AM | 0 | -
8/2 9AM | 407 | No
8/2 10AM | 0 | -

## Slide 14: Additional COP Information for July
There was a request to post more COP information for the month of July for stakeholders
Now posted at http://www.ercot.com/calendar/2018/10/15/144527-QMWG
COPs use Point-In-Time (PIT) logic
  For each row of the data, the PIT_START indicates when the COP data was submitted to ERCOT, and the PIT_STOP indicates when it was either replaced by a subsequent COP submission or was removed from the production system several days after the operating day