## Slide 1
Request for Review of the Reliability Deployment Adders on October 4, 2018
ERCOT Staff
QMWG
November 12, 2018

## Slide 2: Introduction
A request was made to review the resulting reliability deployment price adders on 10/4/2018
In looking at this day and considering previous observations, ERCOT staff has identified some reasons why the reliability deployment price adder values may not necessarily always be intuitive
This presentation focuses on simplified examples to better highlight those reasons and less on the specifics of 10/4/18
  More detailed information for 10/4/18 could be provided during a future meeting, if needed

## Slide 3: SCED Pricing Run Methodology Overview
For RUC-instructed Resources with a telemetered Resource Status of ONRUC and for RMR Resources that are On-Line, set the LSL, LASL, and LDL to zero.
For all other Generation Resources excluding ones with a telemetered status of ONRUC, ONTEST, STARTUP, SHUTDOWN, ONRR, NA, and also excluding RMR Resources that are On-Line and excluding Generation Resources with a telemetered output less than 95% of LSL:
  Set LDL to Max ( LASL, TELEMW - 60*SDRAMP)
  Set HDL to Min ( HASL, TELEMW + 60*SDRAMP)
For CLRs, excluding ones with a telemetered status of OUTL, set LDL and HDL according to protocol 6.5.7.3.1 (2) (c)

## Slide 4: SCED Pricing Run Methodology Overview
Add deployed MW from NCLR and the deployed MW from ERS to GTBD.
Use a linear bid curve defined by a price/quantity pair of $300/MWh for the first MW of Load Resources deployed and a price/quantity pair of $700/MWh for the last MW deployed
Add/subtract the MW from Real-Time DC Tie imports/exports during an EEA in ERCOT/during emergency conditions in the receiving electric grid or to/from GTBD.
Add/subtract the MW from energy delivered to/from ERCOT through registered BLTs during an EEA in ERCOT/or during emergency conditions in the receiving electric grid and to/from GTBD.

## Slide 5: SCED Pricing Run Methodology Overview
Perform the 2-step SCED process with the modified inputs
The Real-Time On-Line Reliability Deployment Price Adder is the minimum of:
  VOLL - DispatchSCED_Systemlambda_Step2 – RTORPA
  Max (0, PricingSCED_Systemlambda_Step2 – DispatchSCED_Systemlambda_Step2)

## Slide 6: Intent of the Pricing Run
Focusing on RUCs, the intent of the pricing run is to account for the “price-taking” energy of the Resource instructed on-line by ERCOT
Looking back at the business case from NPRR626:
  “This NPRR will address the price-reversal impacts of deployment of the following Resources, which do not currently set price:
    ERS
    Reliability Must-Run (RMR) committed units, including units committed for capacity through paragraph (2) of Section 6.5.1.1, ERCOT Control Area Authority (zero – Low Sustained Limit (LSL))
    RUC Committed Units (zero – LSL)
    Deployed MW from Load Resources other than Controllable Load Resources.”
As a result, generally expect to have
  Non-zero adder values when the RUC-instructed Resource is dispatched at its LDL
  Zero adder values when the RUC-instructed Resource is dispatched above its LDL

## Slide 7: Non-Intuitive Cases
There are some reasons why the results may not necessarily fall into this simple expectation
These cases are related to the relaxation of HDLs and LDLs of the Resources that were not RUC-instructed
  The relaxation is intended to avoid ramp limitations that would tend to exaggerate the pricing impacts of the out-of-market action
Descriptions and examples of these are included in the next few slides

## Slide 8: Non-Zero Adders with RUC Resource above LDL
Can be a function of the LDL relaxation of other Resources with limiting ramp rates
The dispatch engine has additional flexibility to dispatch down non-economic capacity
Some of the “price-taking” energy of the Resources that were not RUC-instructed is no longer “price taking” due to additional ramp range
This can lead to higher system lambdas in the pricing run than were observed in the dispatch run

## Slide 9: Zero Adders with RUC Resource at LDL
Can be a function of the HDL relaxation of other Resources with limiting ramp rates
The dispatch engine has additional economic capacity for dispatch
This can lead to lower system lambdas in the pricing run than were observed in the dispatch run
The price adder is floored at $0/MWh to mitigate this effect
As an additional note, RUC-instructed Resources can also be mitigated for SCED Step 2 in both the dispatch and pricing run

## Slide 10: Example 1a – LDL Relaxation
Resource | Shift Factor | LSL | HSL | LDL | HDL | Offer
G1 | -1 | 100 | 500 | 200 | 500 | 75
G2 | 0 | 0 | 1000 | 200 | 1000 | 30
G3 | 0 | 0 | 1000 | 200 | 1000 | 20-30
Load | Shift Factor | MW
L1 | 1 | 225
L2 | 0 | 400
L3 | 0 | 300
Resource | Dispatch Run BP | Dispatch Run LMP | Pricing Run BP | Pricing Run LMP | Adder
G1 | 200 | 25.25 | 175 | 75 | $2.25/MWh
G2 | 200 | 25.25 | 0 | 27.5 | 
G3 | 525 | 25.25 | 750 | 27.5 | 
RUC-Instructed Resource
Limit = 50MW
G1
L1
G2
L2
G3
L3
Ref. Bus

## Slide 11: Example 1b – LDL Relaxation Only the LDL of G1 Relaxed
Resource | Shift Factor | LSL | HSL | LDL | HDL | Offer
G1 | -1 | 100 | 500 | 200 | 500 | 75
G2 | 0 | 0 | 1000 | 200 | 1000 | 30
G3 | 0 | 0 | 1000 | 200 | 1000 | 20-30
Load | Shift Factor | MW
L1 | 1 | 225
L2 | 0 | 400
L3 | 0 | 300
Resource | Dispatch Run BP | Dispatch Run LMP | Pricing Run BP | Pricing Run LMP | Adder
G1 | 200 | 25.25 | 175 | 75 | $0.25/MWh
G2 | 200 | 25.25 | 200 | 25.5 | 
G3 | 525 | 25.25 | 550 | 25.5 | 
RUC-Instructed Resource
Limit = 50MW
G1
L1
G2
L2
G3
L3
Ref. Bus

## Slide 12: Example 2a – LDL Relaxation with a Lower RUC LDL
Limit = 50MW
G1
L1
G2
L2
G3
L3
Ref. Bus
Resource | Shift Factor | LSL | HSL | LDL | HDL | Offer
G1 | -1 | 100 | 500 | 100 | 500 | 75
G2 | 0 | 0 | 1000 | 200 | 1000 | 30
G3 | 0 | 0 | 1000 | 200 | 1000 | 20-30
Load | Shift Factor | MW
L1 | 1 | 225
L2 | 0 | 400
L3 | 0 | 300
Resource | Dispatch Run BP | Dispatch Run LMP | Pricing Run BP | Pricing Run LMP | Adder
G1 | 175 | 75 | 175 | 75 | $2/MWh
G2 | 200 | 25.5 | 0 | 27.5 | 
G3 | 550 | 25.5 | 750 | 27.5 | 
RUC-Instructed Resource

## Slide 13: Example 2b – LDL Relaxation with a Lower RUC LDL Only the LDL of G1 Relaxed
Limit = 50MW
G1
L1
G2
L2
G3
L3
Ref. Bus
Resource | Shift Factor | LSL | HSL | LDL | HDL | Offer
G1 | -1 | 100 | 500 | 100 | 500 | 75
G2 | 0 | 0 | 1000 | 200 | 1000 | 30
G3 | 0 | 0 | 1000 | 200 | 1000 | 20-30
Load | Shift Factor | MW
L1 | 1 | 225
L2 | 0 | 400
L3 | 0 | 300
Resource | Dispatch Run BP | Dispatch Run LMP | Pricing Run BP | Pricing Run LMP | Adder
G1 | 175 | 75 | 175 | 75 | $0/MWh
G2 | 200 | 25.5 | 200 | 25.5 | 
G3 | 550 | 25.5 | 550 | 25.5 | 
RUC-Instructed Resource

## Slide 14: Example 3 – HDL Relaxation
Resource | Shift Factor | LSL | HSL | LDL | HDL | Offer
G1 | -1 | 100 | 500 | 200 | 500 | 75
G2 | 0 | 0 | 1000 | 200 | 500 | 30
G3 | 0 | 0 | 1000 | 200 | 500 | 20-30
Load | Shift Factor | MW
L1 | 1 | 225
L2 | 0 | 400
L3 | 0 | 300
Resource | Dispatch Run BP | Dispatch Run LMP | Pricing Run BP | Pricing Run LMP | Adder
G1 | 200 | 30 | 0 | 29.25 | $0/MWh
G2 | 225 | 30 | 0 | 29.25 | 
G3 | 500 | 30 | 925 | 29.25 | 
RUC-Instructed Resource
Limit = 300MW so not binding
G1
L1
G2
L2
G3
L3
Ref. Bus

## Slide 15: RUC Instructions for 10/4/18
There were 3 Resources that were committed through HRUC during the afternoon of 10/4/18
The QSE for 2 of the Resources opted out of RUC settlement
The 3rd Resource was ONRUC and triggered the reliability deployment pricing run during HE14-19

## Slide 16: Reliability Deployment Price Adders for 10/4/18
Chart: Time
LDL relaxation in pricing run
HDL relaxation in pricing run

## Slide 17: Conclusion
The price adders will fluctuate based on interval-to-interval changes in the system, including changes for Resources that were not RUC-instructed
HDL and LDL relaxation of Resources that were not RUC-instructed is intended to avoid ramp limitations that could exaggerate the pricing impacts of the out-of-market action

## Slide 18: Conclusion
The LDL relaxation can make the price adders higher, even when the RUC-instructed Resource is being dispatched above LDL in the pricing run
  Removing the “price-taking” energy of the Resources that were not RUC-instructed is not necessarily what was intended by the LDL relaxation
On the other side, the HDL relaxation can make the prices adders lower than might otherwise be expected
  Need some method in place to avoid the ramp limitations concern