|  |  |  |  |
| --- | --- | --- | --- |
| NPRR Number | [897](http://www.ercot.com/mktrules/issues/NPRR897) | NPRR Title | Adjustments to Black Start Service (BSS) Procurement Timeline and Testing |
| Date of Decision | November 29, 2018 |
| Action | Recommended Approval |
| Timeline | Normal |
| Proposed Effective Date | December 12, 2018 |
| Priority and Rank Assigned | Not Applicable |
| Nodal Protocol Sections Requiring Revision  | 3.14.2, Black Start8.1.1.2.1.5, System Black Start Capability Qualification and Testing Section 22, Attachment M, Generation Resource Disclosure Regarding Bids for Black Start Service (new) |
| Related Documents Requiring Revision/Related Revision Requests | None |
| Revision Description | This Nodal Protocol Revision Request (NPRR) adjusts the timeline for the Black Start Service (BSS) procurement and testing process, adds a weather limitation disclosure form, and aligns the Load-Carrying Test procedure with actual practice.  |
| Reason for Revision |  Addresses current operational issues. Meets Strategic goals (tied to the [ERCOT Strategic Plan](http://www.ercot.com/content/news/presentations/2013/ERCOT%20Strat%20Plan%20FINAL%20112213.pdf) or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain)*(please select all that apply)* |
| Business Case | Adjusting the BSS bid due date allows more time for Transmission Service Providers (TSPs) to develop Black Start plans after the Black Start Resources have been tested and qualified. This is especially important for first-time bid winners in the Black Start procurement process. The date adjustment moves the Black Start Resource test completion date forward, allowing for Black Start Resource qualification testing to be completed first, confirming capability of the Black Start Resources, prior to the development of the Black Start plan. In current language, the Black Start plan due date is earlier than the Black Start Resource qualification testing due date. This NPRR also adds a weather related limitation disclosure providing a template for Resources bidding for BSS to disclose any limitation that could affect the Resource’s ability to provide BSS. Additionally, the language describing the Load-Carrying Test is adjusted to better align with actual test practice. |
| Credit Work Group | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR897 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |
| PRS Decision | On 9/13/18, PRS voted unanimously to table NPRR897 and refer the issue to ROS. All Market Segments were present for the vote.On 10/18/18, PRS voted to recommend approval of NPRR897 as amended by the 10/15/18 ROS comments as revised by PRS. There was one abstention from the Municipal (DME) Market Segment. All Market Segments were present for the vote.On 11/15/18, PRS voted unanimously to endorse and forward to TAC the 10/18/18 PRS Report and Impact Analysis for NPRR897. All Market Segments were present for the vote. |
| Summary of PRS Discussion | On 9/13/18, participants discussed the revised timelines proposed in NPRR897, whether WMS in addition to ROS should review the NPRR, and that it is preferred that language be in place before the next bid cycle. ERCOT Staff noted that NPRR897 does not revise the bid selection process and poses no market impacts. Participants also discussed the 9/5/18 STEC comments, the subsequent discussion by the Black Start Working Group (BSWG), and that additional comments to NPRR897 are pending.On 10/18/18, participants offered additional language.On 11/15/18, there was no discussion. |
| TAC Decision | On 11/29/18, TAC voted unanimously to recommend approval of NPRR897 as recommended by PRS in the 11/15/18 PRS Report, with a proposed effective date of upon ERCOT Board approval. All Market Segments were present for the vote. |
| Summary of TAC Discussion | On 11/29/18, participants noted the 11/19/18 ERCOT comments requesting an effective date of upon ERCOT Board approval (December 12, 2018) for NPRR897. |
| ERCOT Opinion | ERCOT supports approval of NPRR897. |

|  |
| --- |
| Sponsor |
| Name | Freddy Garcia |
| E-mail Address | Freddy.Garcia@ercot.com |
| Company | ERCOT |
| Phone Number | 512-585-6389 |
| Cell Number |  |
| Market Segment | Not Applicable |

|  |
| --- |
| **Market Rules Staff Contact** |
| **Name** | Brittney Albracht |
| **E-Mail Address** | Brittney.Albracht@ercot.com  |
| **Phone Number** | 512-225-7027 |

|  |
| --- |
| **Comments Received** |
| Comment Author | **Comment Summary** |
| STEC 090518 | Expressed concern that NPRR897 is too broad and threatens ERCOT’s independent evaluation of BSS bids, and proposes new requirements rather than alignment with existing practice; struck existing language “sufficient” in paragraph (3)(c)(iv) of Section 8.1.1.2.1.5 as ambiguous |
| STEC 091418 | Proposed revisions to refine the process surrounding the solicitation and validation of TSP feedback, to clarify what is available as Load during the Load-Carrying Test, and to remove outdated terminology |
| ROS 101518 | Endorsed NPRR897 as amended by the 9/14/18 STEC comments as revised by ROS |
| ERCOT 111918 | Requested an effective date of upon ERCOT Board approval (December 12, 2018) for NPRR897 |

|  |
| --- |
| Market Rules Notes |

Please note the baseline Protocol language in Section 3.14.2 has been updated to reflect the incorporation of NPRR857, Creation of Direct Current Tie Operator Market Participant Role, into the 11/1/18 Protocols.

|  |
| --- |
| Revised Proposed Protocol Language |

3.14.2 Black Start

(1) Each Generation Resource providing BSS must meet the requirements specified in North American Electric Reliability Corporation (NERC) Reliability Standards and the Operating Guides.

(2) Each Generation Resource providing BSS must meet technical requirements specified in Section 8.1.1, QSE Ancillary Service Performance Standards, and Section 8.1.1.1, Ancillary Service Qualification and Testing.

(3) Bids for BSS are due on or before February 15th of each two year period. Bids must be evaluated based on evaluation criteria attached as an appendix to the request for bids and contracted by December 31st for the following two year period. ERCOT shall ensure BSSs are arranged, provided, and deployed as necessary to reenergize the ERCOT System following a Blackout or Partial Blackout.

(a) Resources shall disclose any weather related limitations that could affect the Resource’s ability to provide BSS using the form provided in Section 22, Attachment M, Generation Resource Disclosure Regarding Bids for Black Start Service, as part of a bid to provide BSS.

(b) When a Resource is selected to provide BSS, the Black Start Resource shall be required to complete all applicable testing requirements as specified in Section 8.1.1.2.1.5, System Black Start Capability Qualification and Testing.

(c) ERCOT shall provide a list of all prospective Black Start Resources that responded to the RFP for BSS to the impacted TSPs no later than seven days after the date on which bids for BSS are due. Any feedback from affected TSPs shall be limited to the identification of transmission constraints that may adversely impact the ability of the Black Start Resource to energize the Next Start Resource and shall be due to ERCOT by March 1st of that year. ERCOT shall share the feedback with the QSE representing the prospective Black Start Resource as soon as practicable. The QSE representing the Black Start Resource shall have the option to provide a response to any feedback provided by an affected TSP.

(4) ERCOT may schedule unannounced Black Start testing, to verify that BSS is operable as specified in Section 8.1.1.2.1.5, System Black Start Capability Qualification and Testing.

(5) QSEs representing Generation Resources contracting for BSSs shall participate in training and restoration drills coordinated by ERCOT.

(6) ERCOT shall periodically conduct system restoration seminars for all TSPs, Distribution Service Providers (DSPs), QSEs, Resource Entities and other Market Participants.

|  |
| --- |
| ***[NPRR857: Replace paragraph (6) above with the following upon system implementation:]***(6) ERCOT shall periodically conduct system restoration seminars for all TSPs, Distribution Service Providers (DSPs), Direct Current Tie Operators (DCTOs), QSEs, Resource Entities and other Market Participants. |

(7) ERCOT shall periodically determine and review the location and number of Black Start Resources required, as well as any special transmission or voice communication needs required. ERCOT and providers of this service shall meet the requirements as specified in the Operating Guides and in NERC Reliability Standards.

(8) A Resource Entity representing a Black Start Resource may request that an alternate Generation Resource which is connected to the same black start primary and secondary cranking path as the original Black Start Resource be substituted in place of the original Black Start Resource during the two year term of an executed Standard Form Black Start Agreement (Section 22, Attachment D, Standard Form Black Start Agreement) if the alternate Generation Resource meets testing and verification under established qualification criteria to ensure BSS.

(a) ERCOT, in its sole discretion, may reject a Resource Entity’s request for an alternate Generation Resource and will provide the Resource Entity an explanation of such rejection.

(b) If ERCOT accepts the alternative Generation Resource as the substituted Black Start Resource, such acceptance shall not affect the original terms, conditions and obligations of the Resource Entity under the Standard Form Black Start Agreement. The Resource Entity shall submit to ERCOT an Amendment to Standard Form Black Start Agreement (Section 22, Attachment I, Amendment to Standard Form Black Start Agreement) after qualification criteria has been met.

(9) For the purpose of the Black Start Hourly Standby Fee as described in Section 6.6.8.1, Black Start Hourly Standby Fee, the Black Start Service Availability Reduction Factor shall be determined by using the availability for the original Black Start Resource and any substituted Black Start Resource(s), as appropriate for the rolling 4380 hour period of the evaluation.

(10) Each Generation Resource selected to provide BSS shall be prepared and able to provide BSS at any time as may be required by ERCOT, subject only to the limitations described in ERCOT Protocols or the Black Start Agreement.

8.1.1.2.1.5 System Black Start Capability Qualification and Testing

(1) A Resource is qualified to be a Black Start Resource if it has met the following requirements:

(a) Verified control communication path performance;

(b) Verified primary and alternate voice circuits for receipt of instructions;

(c) Passed the “Basic Starting Test” as defined below;

(d) Passed the “Line-Energizing Test” as defined below;

(e) Passed the “Load-Carrying Test” as defined below;

(f) Passed the “Next Start Resource Test” as defined below;

(g) If not starting itself, has an ERCOT-approved firm standby power contract with deliverability under Blackout circumstances from a non-ERCOT Control Area that can be finalized upon selection as a Black Start Resource;

(h) If not starting itself, has an ERCOT approved agreement with the necessary TSPs for access to another power pool, for coordination of switching during a Blackout or Partial Blackout, for coordination of maintenance through the ERCOT Outage Scheduler for all non-redundant transmission startup feeds;

(i) If dependent upon non-ERCOT transmission resources, agreements providing this Transmission Service have been provided in the proposal; and

(j) Demonstrated to ERCOT’s satisfaction that the Resource has successfully completed remediation to any weather-related limitation disclosed as part of the Black Start Service (BSS) bid.

(2) On successful demonstration of system BSS capability, ERCOT shall certify that the Black Start Resource is capable of providing system BSS capacity and shall provide a copy of the certificate to the Resource Entity of the Black Start Resource. Qualification shall be valid for the time frames set forth below. Except under extenuating circumstances, as reasonably determined by ERCOT, all qualification testing for the next year of BSS must be completed by June 1st of each year.

(3) ERCOT may limit the number of qualification retests allowed. Qualification retesting is required only for the aspect of system BSS capability for which the Black Start Resource failed. If a Black Start Resource under an existing Black Start Agreement does not successfully re-qualify within two months of failing a test described herein, ERCOT shall decertify the Black Start Resource for the remainder of the calendar year as described in Section 7, Black Start Decertification, of Section 22, Attachment D, Standard Form Black Start Agreement. The following tests are required for BSS qualification:

(a) The “Basic Starting Test” includes the following:

(i) The basic ability of the Black Start Resource to start itself, or start from a normally open interconnection to another provider not inside the ERCOT interconnection, without support from the ERCOT System;

(ii) Annual testing, either as a stand-alone test or part of the Line Energizing and Load-Carrying Tests, and the test is performed during a one-week period agreed to in advance by the Black Start Resource and ERCOT and must not cause outage to ERCOT Customer Load or the availability of other Resources to the ERCOT market;

(iii) Confirmation of the dates of the test with the Black Start Resource by ERCOT;

(iv) Isolation of the Black Start Resource, including all auxiliary Loads, from the ERCOT System, except for the transmission that connects the Resource to a provider not inside the ERCOT interconnection if the startup power is supplied by a firm standby contract. Black Start Resources starting with the assistance of a provider not inside the ERCOT interconnection through a firm standby agreement will connect to provider not inside the ERCOT interconnection, start-up, carry internal Load, disconnect from the provider not inside the ERCOT interconnection if not supplied through a black-start capable DC Tie, and continue equivalently to what is required of other Black Start Resources;

(v) The ability of the Black Start Resource to start without assistance from the ERCOT System, except for the transmission that connects the Resource to a provider not inside the ERCOT interconnection if the startup power is supplied by a firm standby contract;

(vi) The ability of the Black Start Resource to remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or Loads in the immediate area for at least 30 minutes;

(vii) The Black Start Resource must have verified that its Volts/Hz relay, over-excitation limiter, and under-excitation limiter are set properly and that no protection devices will trip the Black Start Resource within the required reactive range. The Resource Entity for the Black Start Resource shall provide ERCOT with data to verify these settings; and

(viii) Each Black Start Resource must pass a Basic Starting Test once each calendar year.

(b) The “Line-Energizing Test” must be conducted at a time agreed on by the Black Start Resource, TSP or Distribution Service Provider (DSP), and ERCOT and includes the following:

(i) Energizing transmission with the Black Start Resource when conditions permit as determined by the TSP or DSP but at least once every three years;

(ii) De-energizing sufficient transmission in such manner that when energized by the Black Start Resource it demonstrates the Black Start Resource’s ability to energize enough transmission to deliver to the Loads the Resource’s output that ERCOT’s restoration plan requires the Black Start Resource to supply. ERCOT shall be responsible for transmission connections and operations that are compatible with the capabilities of the Black Start Resource;

(iii) Conducting a Basic Starting Test;

(iv) Energizing transmission with the Black Start Resource of the previously de-energized transmission, while monitoring frequency and voltages at both ends of the line. Alternatively, if ERCOT agrees, the transmission line may be connected to the Black Start Resource before starting, allowing the Resource to energize the line as it comes up to speed;

(v) Stable operation of the Black Start Resource (in both frequency and voltage) while supplying only its auxiliary Loads or external Loads for at least 30 minutes;

(vi) This test may be performed together with the Basic Starting Test in one 30 minute interval; and

(vii) Each Black Start Resource must pass a Line-Energizing Test once every three years.

(c) The “Load-Carrying Test” shall utilize the Load agreed to between ERCOT, TSP and the Black Start Resource. Testing shall occur as conditions permit, at a time agreed on by the Black Start Resource, TSP or DSP, and ERCOT, and includes the following:

(i) Stable operation of the Black Start Resource (in both frequency and voltage) while supplying restoration power to Load that is not identified as auxiliary Load of the Resource and is allowed to be auxiliary Load of adjacent facilities;

(ii) Conducting a Basic Starting Test;

(iii) Conducting a Line-Energizing Test when required;

(iv) Under the direction of ERCOT or the TSP operator, the Black Start Resource shall demonstrate the Black Start Resource’s capability to supply the required Load, while maintaining voltage and frequency for at least 30 minutes;

(v) This test may be performed together with the Basic Starting Test and Line Energizing Test when required in one 30 minute interval; and

(vi) Qualification under the Load-Carrying Test is valid for five years.

(d) “Next Start Resource Test”:

(i) The ability of a Black Start Resource to start up the next start unit’s largest required motor while continuing to remain stable and control voltage and frequency shall be tested. This test shall be repeated when a new next start unit is selected;

(ii) To pass the test:

(A) The potential Black Start Resource must start the next start unit (as determined by ERCOT), or start the next start unit’s largest required motor and satisfied the next start unit’s minimum startup Load requirements; or

(B) The Resource Entity shall demonstrate to the satisfaction of ERCOT through simulation studies conducted by the Resource Entity or a qualified third party, that the potential Black Start Resource is capable of starting the next start unit’s largest required motor while meeting the next start unit’s minimum startup Load requirements.

(iii) Potential Black Start Resources may request from ERCOT the information detailed in paragraph (3)(d)(ii)(B) above of the next start unit prior to the satisfaction of this requirement. ERCOT shall request this information from the designated next start unit. Such data, if requested by ERCOT, shall be provided by the QSE or Resource Entity representing the next start unit to ERCOT within 30 days. Such information shall be considered Protected Information by the requesting Resource Entity;

(iv) If a physical test is performed, the test shall commence with a Basic Starting Test, followed by a Line Energizing Test when required and a Load-Carrying Test as a stand-alone test or part of the Next Start Resource Test;

(v) If a physical test is performed, the Black Start Resource must remain stable (in both voltage and frequency) and controlling voltage for 30 minutes;

(vi) If a physical test is performed, this test may be performed together with the Basic Starting Test, Line Energizing Test when required, and Load-Carrying Test in one 30 minute interval; and

(vii) Each Black Start Resource must pass the Next Start Resource Test once every five years.

(4) Each qualified Black Start Resource shall perform a Black Start Resource Availability Test quarterly unless the Black Start Resource has successfully started and operated at LSL or higher for at least four consecutive Settlement Intervals during the quarter. The Black Start Resource’s cost to perform a Black Start Availability Test may be a component of the overall bid for BSS but ERCOT will not separately compensate QSEs representing Black Start Resources for such testing. ERCOT, at its sole discretion, may grant an exemption of the Black Start Resource Availability Test for QSEs whose Black Start Resources have responded as instructed by ERCOT during an EEA event.

(5) The Black Start Resource Availability Test shall be scheduled by ERCOT. Upon receipt of notification for a Black Start Resource Availability Test, the QSE representing the Black Start Resource shall send confirmation to ERCOT of its intent to comply with the test or submit a request to reschedule along with justification for the request.

(6) ERCOT shall provide the QSE representing the Black Start Resource two-hour notice in order to allow the QSE time to update its COP. The QSE representing the Black Start Resource shall show the Resource as “ONTEST” in its COP and through its Real-Time telemetry for the duration of the test. As part of the Black Start Resource Availability Test, the QSE representing the Black Start Resource shall start the Black Start Resource and operate it at or above its LSL for at least four consecutive Settlement Intervals. After completion of the Black Start Resource Availability Test the QSE will update its COP to reflect their current status.

(7) Upon completion of the Black Start Resource Availability Test, the QSE representing the Black Start Resource shall complete and file a Black Start Resource Availability Test report with ERCOT. If the Black Start Resource wants to use a successful start and normal operation to satisfy the quarterly reporting requirement, it must provide the necessary information for the start and normal operation on a Black Start Resource Availability Test report. The report form shall be provided by ERCOT.

(8) A Black Start Resource Availability Test is deemed to be successful if the Black Start Resource comes On-Line within the time specified in the Black Start Resource’s RFP response submitted to ERCOT and operates at a minimum level as agreed to by ERCOT and the QSE representing the Black Start Resource for at least four consecutive Settlement Intervals.

(9) If the Black Start Resource fails to successfully start during the Black Start Resource Availability Test, the QSE representing the Black Start Resource shall immediately update its Availability Plan for that Black Start Resource showing zero availability. The QSE representing the Black Start Resource shall not receive the Hourly Standby Fee for BSS effective from the date of the failed Black Start Resource Availability Test. The QSE representing the Black Start Resource may schedule a second Black Start Resource Availability Test, subject to ERCOT approval, to be completed within ten Business Days of the date of the failed Black Start Resource Availability Test unless a later date is agreed to by ERCOT. The cost of the second Black Start Resource test will be borne solely by the QSE representing the Black Start Resource.

(10) If the Black Start Resource successfully passes the second Black Start Resource Availability Test, the QSE representing the Black Start Resource shall resume receipt of the Hourly Standby Fee beginning on the date of the successful Black Start Resource Availability Test.

(11) If the Black Start Resource fails a second Black Start Resource Availability Test within the quarter, it shall immediately be disqualified from providing BSS and shall receive no further compensation under the Black Start Service Agreement. In addition, ERCOT shall claw-back all Hourly Standby Fee payments made to the QSE representing the Black Start Resource since its last successful Black Start Resource Availability Test or its last successful start and operation under normal system conditions, whichever is later. The clawed-back Hourly Standby Fee payments shall be uplifted by ERCOT to Loads on a Load Ratio Share (LRS) basis. ERCOT may, at its sole discretion, consider allowing the Black Start Resource to perform an additional Black Start Resource Availability Test. ERCOT may also, at its sole discretion, seek to procure additional Black Start Resources to replace the disqualified Black Start Resource.

(12) A QSE representing the Black Start Resource shall update its Availability Plan for a Black Start Resource to show zero if the Black Start Resource fails to perform when ERCOT has issued a Dispatch Instruction to come On-Line any time other than for a Blackout. The Black Start Resource shall continue to be shown as unavailable until it successfully starts under normal operations or completes a successful Black Start Resource Availability Test.

(13) If the Black Start Resource fails to perform successfully during an actual Blackout and the Black Start Resource has been declared available, as defined in Section 22, Attachment D, ERCOT shall:

(a) Decertify the Black Start Resource for the remainder of the Black Start Agreement contract term, and

(b) Claw-back 100% of the Hourly Standby Fee paid to the QSE representing the Black Start Resource for all the Operating Days since its last successful Black Start Resource Availability Test or its last successful start and operation under normal system conditions, whichever is later.

**ERCOT Nodal Protocols**

**Section 22**

**Attachment M: Generation Resource Disclosure Regarding Bids for Black Start Service**

**TBD, 20XX**

**Generation Resource Disclosure regarding Bids for Black Start Service**

**Resource Entity:**

**Qualified Scheduling Entity (QSE) representing the Resource Entity:**

**Generation Resource (list by Resource Site Code):**

**Operational Weather limitations:**

(1) Minimum Ambient Operation Temperature (°F) \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(2) Maximum Ambient Operation Temperature (°F) \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(3) Relative Humidity (%)\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

**Weather Related Limitation Disclosure:**

Please list any weather-related limitations to the Generation Resource’s start-up/operation capabilities (include a brief description of the limitation(s), planned remediation for the limitation, and an associated target completion date for the remediation): \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

**Weatherization affirmation – please affirm by checking the box:**

[\_] I hereby affirm that all disclosed weather related limitations listed above and weatherization preparations for equipment critical to providing Black Start service are complete or will be completed prior to the beginning of Black Start Qualification Testing.

By signing below, I certify that I am an officer or authorized executive of each Resource Entity listed above, that I am authorized to execute and submit this declaration on behalf of each Resource Entity listed above, and that the statements contained herein are true and correct.

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Signature

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Name

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Title

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Date