## TitlePage
Report on the Capacity, Demand and Reserves
(CDR) in the ERCOT Region, 2019-2028
December 4, 2018

## Contents
Table of Contents
Tab | Notes
Disclaimer | Please read
Changes from previous CDR | List of significant changes relative to the last CDR, published May 2018
Definitions | List of definitions
Executive Summary | Synopsis of considerations for this report
SummerSummary | Shows load forecast, resource capacity and reserve margin for Summer 2019 through Summer 2023
SummerCapacities | List of registered resources and capabilities used in determining the capacity contribution for Summer Peak Season
SummerFuelTypes | Lists generation fuel types by MW and by percentage for Summer 2019 through Summer 2023
WinterSummary | Shows load forecast, resource capacity and reserve margin for Winter 2018/2019 through Winter 2022/2023
WinterCapacities | List of registered resources and capabilities used in determining the capacity contribution for Winter Peak Season
WinterFuelTypes | Lists generation fuel types by MW and by percentage for Winter 2018/2019 through Winter 2022/2023
Supplemental | Shows the capacity of proposed generation resources for the summer of each forecast year based on meeting various interconnection process milestones. Also shows the load forecast, resource capacity and reserve margin for both Summer and Winter seasons for the later half of the CDR forecast period.

## Disclaimer
Disclaimer
FOR PLANNING PURPOSES ONLY
This ERCOT report has been prepared for specific ERCOT and Market Participant purposes and has been developed from data provided by ERCOT Market Participants. The data may contain errors or become obsolete at the time of this report's release. ERCOT MAKES NO WARRANTY, EXPRESS OR IMPLIED, INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE, AND DISCLAIMS ANY AND ALL LIABILITY WITH RESPECT TO THE ACCURACY OF SAME OR THE FITNESS OR APPROPRIATENESS OF SAME FOR ANY PARTICULAR USE. THIS ERCOT REPORT IS SUPPLIED WITH ALL FAULTS. Readers of this report should independently verify the accuracy, reliability, completeness, currency, and suitability for any particular purpose of any information in this report.

## Changes
Notes on Changes Relative to the Last CDR, Published May 2018
1 | Wind Summer Peak Average Capacity Contribution Percentages (WINDPEAKPCT) were updated to include summer 2018 data. The Non-coastal region increased from 14% to 15% and the Coastal region decreased from 59% to 58%.
2 | The solar Summer Peak Average Capacity Contribution Percentage (SOLAR_PEAK_PCT) decreased from 75% to 74% after being updated for summer 2018 data.
3 | The following Planned Resources have been moved to Operational Status since the release of the May 2018 CDR report:
| Project Name | Unit Code | County | Fuel | Zone | Installed Capacity MW | Summer Capacity MW
| PHR PEAKERS (BAC) | BAC_CTG | GALVESTON | GAS | GALVESTON | 329 | 329
| DENTON ENERGY CENTER | DEC_AGR | DENTON | GAS | NORTH | 226 | 226
| FRIENDSWOOD G | FEGC_UNIT1 | HARRIS | GAS | HOUSTON | 119 | 119
| FLAT TOP WIND I | FTWIND_UNIT_1 | MILLS | WIND | NORTH | 200 | 30
| HICKMAN (SANTA RITA WIND) | HICKMAN | REGAN AND IRION | WIND | WEST | 300 | 45
| RTS WIND | RTS_U1 | MCCULLOCH | WIND | SOUTH | 160 | 24
| CASTLE GAP SOLAR | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 180 | 133.2
| RIGGINS (SE BUCKTHORN WESTEX SOLAR) | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 150 | 111
| SOLAIREHOLMAN 1 | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 50 | 37
| TOTAL |  |  |  |  | 1714 | 1054.2
4 | The following Planned Resources have met the requirements to be added to the CDR report (Signed SGIA, acquisition of required air emission permits, submission of proof of adequate water supplies for thermal units):
| Project Name | GENERATION INTERCONNECTION PROJECT CODE | County | Fuel | Zone | Year of Projected Commercial Operations 1/ | Capacity MW | Summer Capacity MW
| VICTORIA PORT (VICTPORT) | 17INR0045 | CALHOUN | GAS | COASTAL | 2019 | 100 | 100
| ARMSTRONG WIND | 18INR0029 | ARMSTRONG | WIND | PANHANDLE | 2020 | 253 | 37.95
| BARROW RANCH (JUMBO HILL WIND) | 18INR0038 | ANDREWS | WIND | WEST | 2019 | 160 | 24
| BLUE SUMMIT II | 18INR0070 | WILBARGER | WIND | WEST | 2019 | 102 | 15.3
| CANYON WIND | 18INR0030 | SCURRY | WIND | WEST | 2020 | 300.9 | 45.135
| DARMSTADT | 18INR0023 | SCHLEICHER | WIND | WEST | 2019 | 200.9 | 30.135
| EASTER WIND | 15INR0063 | CASTRO | WIND | PANHANDLE | 2020 | 307.5 | 46.125
| HART WIND | 16INR0033 | CASTRO | WIND | PANHANDLE | 2020 | 150 | 22.5
| KONTIKI 1 WIND | 19INR0099a | GLASSCOCK | WIND | WEST | 2019 | 255.3 | 38.295
| KONTIKI 2 WIND | 19INR0099b | GLASSCOCK | WIND | WEST | 2020 | 255.3 | 38.295
| MAVERICK CREEK I | 20INR0045 | CONCHO | WIND | WEST | 2020 | 252 | 37.8
| MAVERICK CREEK II | 20INR0046 | CONCHO | WIND | WEST | 2020 | 252 | 37.8
| MESTENO WIND | 16INR0081 | STARR | WIND | SOUTH | 2019 | 201.6 | 30.24
| NORTHDRAW WIND | 13INR0025 | RANDALL | WIND | PANHANDLE | 2019 | 150 | 22.5
| OVEJA WIND | 18INR0033 | IRION | WIND | WEST | 2019 | 300 | 45
| PRAIRIE HILL WIND | 19INR0100 | LIMESTONE | WIND | NORTH | 2020 | 300 | 45
| RANCHERO WIND | 20INR0011 | CROCKETT | WIND | WEST | 2019 | 300 | 45
| TG EAST WIND | 19INR0052 | KNOX | WIND | WEST | 2019 | 275.6 | 41.34
| VERA WIND | 19INR0051 | KNOX | WIND | WEST | 2019 | 242.8 | 36.42
| CHALUPA WIND | 20INR0042 | CAMERON | WIND-C | COASTAL | 2020 | 174 | 100.92
| CRANEL WIND | 19INR0112 | REFUGIO | WIND-C | COASTAL | 2019 | 220 | 127.6
| LAS MAJADAS WIND | 17INR0035 | WILLACY | WIND-C | COASTAL | 2020 | 272.8 | 158.224
| RAYMOND WIND | 18INR0059 | WILLACY | WIND-C | COASTAL | 2019 | 201.6 | 116.928
| ARAGORN SOLAR | 19INR0088 | CULBERSON | SOLAR | WEST | 2020 | 186.3 | 137.862
| HOLSTEIN SOLAR | 19INR0009 | NOLAN | SOLAR | WEST | 2020 | 204 | 150.96
| LONG DRAW SOLAR | 18INR0055 | BORDEN | SOLAR | WEST | 2020 | 225 | 166.5
| MISAE SOLAR | 18INR0045 | CHILDRESS | SOLAR | PANHANDLE | 2019 | 240.8 | 178.192
| OBERON SOLAR | 19INR0083 | ECTOR | SOLAR | WEST | 2019 | 180 | 133.2
| PHOEBE SOLAR | 19INR0029 | WINKLER | SOLAR | WEST | 2019 | 250 | 185
| QUEEN SOLAR | 19INR0102 | UPTON | SOLAR | WEST | 2019 | 400 | 296
| RAMBLER SOLAR | 19INR0114 | TOM GREEN | SOLAR | WEST | 2019 | 150 | 111
| SODA LAKE SOLAR 1 | 18INR0040 | CRANE | SOLAR | WEST | 2020 | 200 | 148
| SODA LAKE SOLAR 2 | 20INR0143 | CRANE | SOLAR | WEST | 2020 | 200 | 148
| TOTAL | [5 empty] | 7463.4 | 2897.221
1/ This date is based on the projected Commercial Operations Date (COD) reported by the project developer. In contrast, a unit's first summer CDR forecast year (reported in the SummerCapacities sheet) is defined as the first year in which the capacity is available for the entire summer Peak Load Season. (The summer Peak Load Season constitutes the months of June, July, August and September.) For example, if a unit has a projected COD of July 1, 2015, the first summer CDR forecast year would be 2016.
5 | Recently cancelled planned projects: Natural Gas: 785 MW Pinecrest Energy Center Project had a projected COD of April 2020 and was cancelled on 9/21/18. 654 MW Indeck Wharton Energy Center had a projected COD of Sep 2021 and was cancelled 9/4/2018 324 MW Bethel CAES Project had a projected COD of Nov 2020 and was cancelled on 9/7/2018. Wind: 300 MW Pullman Road Wind had a projected COD of Oct 2019 and was cancelled on 8/29/2018. 218 MW Mariah Del Sur had a projected COD of Dec 2018 and was cancelled on 8/31/2018. 203 MW Unity Wind had a projected COD of Oct 2019 and was cancelled on 9/21/2018. 188 MW Grandview Wind 3 (Conway) had a projected COD of Dec 2019 and was cancelled on 10/9/2018. 160 MW Longhorn South had a projected COD of Dec 2020 and was cancelled on 8/29/2018.
6 | The following units moved from Operational status to Seasonal Mothballed status: SPENCER (STG U4, STG U5) [118 MW] as of 10/3/2018 (operation period Jun 1st to Sep 30th)
7 | The following units moved from Operational status to Mothballed status: GIBBONS CREEK U1 (GIBCRK_GIB_CRG1) [470 MW] on 10/1/18. (scheduled to return between May-June 2019)
8 | Seasonal capacity ratings for battery energy storage systems are now being listed in the 'SummerCapacities' and 'WinterCapacities' worksheets. These resources are not included in the reserve margin calculations in the 'Summary' worksheets because they are assumed to provide regulation reserves rather than sustained capacity available to meet peak loads.
9 | Capacity changes due to planned repower projects are reflected in the operational units' ratings upon project completion.

## Definitions
Definitions
Available Mothballed Capacity based on Owner's Return Probability
Mothballed capacity with a return-to-service probability of 50% or greater for a given season of the year, as provided by its owner, constitutes available mothballed generation. Return probabilities for individual units are considered protected information under the ERCOT Protocols and therefore are not included in this report.
Energy Efficiency Program Savings Forecast
ERCOT's energy efficiency forecast uses the PUCT's annual verified energy efficiency program savings estimates as the starting point. (See the definition for verified energy efficiency program savings below.) Annual incremental growth in energy efficiency savings is calculated by multiplying ERCOT's peak load forecast by an energy efficiency penetration factor. The current factor is 0.0018, and is derived using the following assumptions: · The unadjusted penetration rate for energy efficiency is 0.4% of total load for all residential and commercial consumers (including NOIEs) · A 50% adjustment is applied to account for actual program effectiveness and program savings that may already be accounted for in the load forecast model · A 90% adjustment is applied to represent the proportion of the total load forecast that is commercial and residential customers Energy efficiency impacts from meeting the Texas Legislature's goals are assumed to accumulate for seven years from the time that the annual goals must first be met (December 31, 2013). Finally, ERCOT incorporates annual energy efficiency estimates from municipal utilities and electric cooperatives provided to the State Energy Conservation Office (SECO) or directly to ERCOT. Annual SECO report submission by these entities is required under S.B. No. 924. If annual reports for the previous calendar year are not available at the time the CDR is prepared, ERCOT incorporates report data for the most recently available reporting year. If energy efficiency capacity amounts are not grossed up to reflect avoided distribution and transmission (T&D) line losses, then ERCOT applies an 8% gross-up factor. The gross-up factor comes from ERCOT's annual Transmission and Distribution Loss Factors reports.
Mothballed Unit
A generation resource for which a generation entity has submitted a Notification of Suspension of Operations, for which ERCOT has declined to execute an RMR agreement, and for which the generation entity has not announced retirement of the generation resource. A seasonal mothballed unit is one in which the generation entity requests a seasonal operation period that must include the summer Peak Load Season, June 1 through September 30.
Mothballed Capacity
Capacity that is designated as mothballed by a generating unit's owner as described above, and which is not available for operations during the summer Peak Load Season (June, July, August and September) or winter Peak Load Season (December, January and February).
Forecast Zone
Forecast Zones generally have the same boundaries as the 2003 Congestion Management Zones with the following exceptions: A) Panhandle Zone for resources in the Texas Panhandle counties and outside the 2003 Congestion Management Zones, and B) Coastal Zone for resources in 11 counties along the Texas Gulf Coast and formerly in the South Zone of the 2003 Congestion Management Zones.
Full Interconnection Study (FIS)
The set of studies conducted by a Transmission Service Provider (TSP) for the purpose of identifying any electric system improvements or enhancements required to reliably interconnect a new All-Inclusive Generation Resource consistent with the provisions of Planning Guide Section 5, Generation Resource Interconnection or Change Request. These studies may include steady-state studies, system protection (short-circuit) studies, dynamic and transient stability studies, facility studies, and sub-synchronous oscillation studies.
LRs (Load Resources)
Load capable of reducing or increasing the need for electrical energy or providing Ancillary Services to the ERCOT System, as described in the ERCOT Protocols, Section 3.6, Load Participation. These Resources may provide the following Ancillary Services: Regulation Up Service, Regulation Down Service, Responsive Reserve Service, and Non-Spinning Reserve Service. The Resources must be registered and qualified by ERCOT and will be scheduled by a Qualified Scheduling Entity (QSE).
Peak Load Seasons
Summer months are June, July, August, and September; winter months are December, January, and February.
Private Use Networks
An electric network connected to the ERCOT transmission grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation).
Non-Synchronous Tie
A non-synchronous transmission interconnection between ERCOT and non-ERCOT electric power systems.
Reliability Must-Run (RMR) Unit
A generation resource unit operated under the terms of an agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria.
Signed SGIA (Standard Generation Interconnection Agreement)
An agreement that sets forth requirements for physical connection between an eligible transmission service customer and a transmission or distribution service provider.
Switchable Generation Resource (SGR)
A generation resource that can be connected to either the ERCOT transmission grid or a grid outside the ERCOT Region.
Verified Energy Efficiency Program Savings
The total megawatt (MW) amount of verified peak load capacity reductions due to residential and commercial sector energy efficiency incentive programs that are reported by electric utilities in the ERCOT Region to the Public Utility Commission of Texas. See Utilities Code Section 39.905.
Wind Peak Average Capacity Contribution
The seasonal net capacity rating of wind resources multiplied by the Seasonal Peak Average Capacity Percentage for non-coastal and coastal regions.
Wind Seasonal Peak Average Capacity Percentage
The average wind capacity available for the summer and winter Peak Load Seasons for a region (non-coastal / coastal) divided by the installed capacity for the region, expressed as a percentage. Details for the derivation of the percentages are outlined in ERCOT Protocol Section 3.2.6.2.2 (see http://www.ercot.com/content/wcm/current_guides/53528/03-110118_Nodal.docx).
Wind Regions
The coastal wind region comprises the following 11 Texas counties along the southern Gulf Coast: Cameron, Willacy, Kenedy, Kleberg, Nueces, San Patricio, Refugio, Aransas, Calhoun, Matagorda, and Brazoria. The non-coastal region consists of all other counties in the ERCOT Region.
Capacity Pending Retirement
Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2.

## Executive_Summary
CDR Report - Executive Summary
* An ERCOT Weather Zone map is available at: | http://www.ercot.com/about/weather
Based on updates to ERCOT's load forecast and resource availability, planning reserve margins are projected to be lower than those cited in the May 2018 CDR report. For example, the 2019 summer reserve margin is projected to be 8.1%, a reduction of 2.9 percentage points. The reserve margin decreases are primarily due to higher expected seasonal peak loads along with additional delays and cancellations of planned projects.
This CDR report is based on a new long-term load forecast prepared in November 2018. The 2019 summer peak load is now projected to be 74,853 MW, reflecting a 651 MW increase relative to the load forecast prepared in November 2017. This increase is mainly driven by greater oil and gas production in the Far West Weather Zone.* For later years, expectations for greater economic growth in the Coast and South Central Weather Zones contribute most of the peak load difference between forecasts. Additionally, the forecast for Emergency Response Service (ERS) capacity decreased by 350 MW, resulting in a corresponding increase in the firm peak load forecast.
Regarding planned generation projects, three gas-fired projects totaling 1,763 MW and five wind projects totalling 1,069 MW were cancelled since the release of the May 2018 CDR report. Delayed projects include a 419 MW gas-fired resource whose in-service date has been moved to June 2021 as well as several planned wind and solar projects with a total summer peak average capacity contribution of 551 MW. The total installed capacity of the delayed renewable projects was 2,066 MW. Also contributing to lower reserve margins was a decrease in capacity ratings for several operational gas-fired units, totalling 402 MW.
Since the release of the May 2018 CDR report, resources totaling 1,714 MW have been approved by ERCOT for commercial operations. Wind and solar resource installed capacity represents 1,040 MW of this total, translating to an expected summer peak average capacity contribution of 380 MW. The remaining 674 MW consists of three gas-fired plants. Planned resources that became newly eligible for inclusion in this CDR report total 7,463 MW of installed capacity, including 5,127 MW of wind resources, 2,236 MW of solar resources, and 100 MW of gas resources.
The methodology for developing most of this report is defined in Section 3.2.6 of the ERCOT Protocols (see: http://www.ercot.com/content/wcm/current_guides/53528/03-110118_Nodal.docx). Market Participant information available to ERCOT as of November 30, 2018, is reflected in the report.

## SummerSummary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Summer Summary: 2019-2023
Load Forecast, MW: |  | 2019 | 2020 | 2021 | 2022 | 2023
| Summer Peak Demand (based on normal weather) | 74853.2073 | 76845.4656 | 78823.7416 | 80454.5979 | 82101.3718
| plus: Energy Efficiency Program Savings Forecast | 1543.7865 | 1822.0386 | 2103.9244 | 2389.4438 | 2678.597
| Total Summer Peak Demand (before Reductions from Energy Efficiency Programs) | 76396.9938 | 78667.5042 | 80927.666 | 82844.0417 | 84779.9688
| less: Load Resources providing Responsive Reserves | -1125.06 | -1125.06 | -1125.06 | -1125.06 | -1125.06
| less: Load Resources providing Non-Spinning Reserves | 0 | 0 | 0 | 0 | 0
| less: Emergency Response Service (10- and 30-min ramp products) | -772.9968 | -753.0048 | -753.0048 | -753.0048 | -753.0048
| less: TDSP Standard Offer Load Management Programs | -281.5608 | -281.5608 | -281.5608 | -281.5608 | -281.5608
| less: Energy Efficiency Program Savings Forecast | -1543.7865 | -1822.0386 | -2103.9244 | -2389.4438 | -2678.597
| Firm Peak Load, MW | 72673.5897 | 74685.84 | 76664.116 | 78294.9723 | 79941.7462
Resources, MW: |  | 2019 | 2020 | 2021 | 2022 | 2023
| Installed Capacity, Thermal/Hydro | 65421.7748 | 65786.7748 | 65863.7748 | 65863.7748 | 65863.7748
| Switchable Generation Resource Capacity, MW | 3515.8 | 3515.8 | 3515.8 | 3515.8 | 3515.8
| less: Switchable Capacity Unavailable to ERCOT, MW | -789.2 | -843.8 | -543.8 | -543.8 | -543.8
| Available Mothballed Capacity, MW | 118 | 118 | 118 | 0 | 0
| Capacity from Private Use Networks | 3324.9495 | 3288.9495 | 3259.9495 | 3319.9495 | 3319.9495
| Non-Coastal Wind, Peak Average Capacity Contribution (15%) | 2837.37 | 2837.37 | 2837.37 | 2837.37 | 2837.37
| Coastal Wind, Peak Average Capacity Contribution (58%) | 1519.368 | 1519.368 | 1519.368 | 1519.368 | 1519.368
| Solar Utility-Scale, Peak Average Capacity Contribution (74%) | 1099.196 | 1099.196 | 1099.196 | 1099.196 | 1099.196
| Storage, Peak Average Capacity Contribution (0%) | 0 | 0 | 0 | 0 | 0
| RMR Capacity to be under Contract | 0 | 0 | 0 | 0 | 0
| Capacity Pending Retirement, MW | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, MW | 77047.2583 | 77321.6583 | 77669.6583 | 77611.6583 | 77611.6583
| Capacity Contribution - Non-Synchronous Ties, MW | 429.6 | 429.6 | 429.6 | 429.6 | 429.6
| Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 301 | 301 | 1925.7 | 1925.7 | 1925.7
| Planned Non-Coastal Wind with Signed IA, Peak Average Capacity Contribution (15%) | 235.605 | 1315.455 | 1699.56 | 1699.56 | 1699.56
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution (58%) | 342.142 | 990.408 | 1249.552 | 1249.552 | 1249.552
| Planned Solar Utility-Scale, Peak Average Capacity Contribution (74%) | 199.356 | 2293.408 | 3041.77 | 3041.77 | 3041.77
| Planned Storage, Peak Average Capacity Contribution (0%) | 0 | 0 | 0 | 0 | 0
| Total Capacity, MW | 78554.9613 | 82651.5293 | 86015.8403 | 85957.8403 | 85957.8403
| Reserve Margin | 8.093% | 10.67% | 12.2% | 9.787% | 7.526%
(Total Resources - Firm Load Forecast) / Firm Load Forecast

## SummerCapacities
Unit Capacities - Summer
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | IN-SERVICE YEAR | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 437
12 | GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470
13 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
14 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785
15 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824
16 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836
17 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
18 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805
19 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805
20 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840
21 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825
22 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
23 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
24 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 940 | 940 | 940 | 940 | 940 | 940 | 940 | 940 | 940 | 940
25 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
26 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
27 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664
28 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663
29 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
30 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
31 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
32 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
33 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
34 | BARNEY M DAVIS REPOWER CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
35 | BARNEY M DAVIS REPOWER CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
36 | BARNEY M DAVIS REPOWER STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
40 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9
41 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4
42 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9
43 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2
44 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 214.9 | 214.9 | 214.9 | 214.9 | 214.9 | 214.9 | 214.9 | 214.9 | 214.9 | 214.9
45 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
46 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
47 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
48 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
49 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
50 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
51 | CALHOUN (PORT COMFORT) 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS | COASTAL | 2017 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
52 | CALHOUN (PORT COMFORT) 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS | COASTAL | 2017 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
53 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
54 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
55 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
56 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
57 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62
58 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101
59 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
60 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
61 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
62 | COLORADO BEND II CT7 |  | CBECII_CT7 | WHARTON | GAS | SOUTH | 2017 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325
63 | COLORADO BEND II CT8 |  | CBECII_CT8 | WHARTON | GAS | SOUTH | 2017 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325
64 | COLORADO BEND II ST8 |  | CBECII_STG9 | WHARTON | GAS | SOUTH | 2017 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440
65 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
66 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
67 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
68 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
69 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
70 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
71 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
72 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
73 | DEER PARK ENERGY CENTER STG |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
74 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
75 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
76 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
77 | FERGUSON REPLACEMENT CTG1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
78 | FERGUSON REPLACEMENT CTG2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
79 | FERGUSON REPLACEMENT STG |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
80 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
81 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
82 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
83 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
84 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
85 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
86 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406
87 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406
88 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6
89 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6
90 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2 | 176.2
91 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7
92 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7
93 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5 | 174.5
94 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS | COASTAL | 2000 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
95 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS | COASTAL | 2000 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
96 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS | COASTAL | 2000 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
97 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
98 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
99 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
100 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
101 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
102 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
103 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
104 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
105 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
106 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213
107 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
108 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
109 | HIDALGO ENERGY CENTER STG |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172
110 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2006 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
111 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2006 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
112 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2006 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
113 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
114 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
115 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
116 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
117 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
118 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
119 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
120 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
121 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
122 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
123 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
124 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
125 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
126 | LOST PINES POWER STG |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
127 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6
128 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6 | 208.6
129 | MAGIC VALLEY STATION STG |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253
130 | MIDLOTHIAN ENERGY FACILITY CS 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229
131 | MIDLOTHIAN ENERGY FACILITY CS 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227
132 | MIDLOTHIAN ENERGY FACILITY CS 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227
133 | MIDLOTHIAN ENERGY FACILITY CS 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227
134 | MIDLOTHIAN ENERGY FACILITY CS 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241
135 | MIDLOTHIAN ENERGY FACILITY CS 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243
136 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
137 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
138 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
139 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149
140 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
141 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 145.3 | 145.3 | 145.3 | 145.3 | 145.3 | 145.3 | 145.3 | 145.3 | 145.3 | 145.3
142 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7
143 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9
144 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9
145 | PANDA SHERMAN POWER CTG1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196
146 | PANDA SHERMAN POWER CTG2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
147 | PANDA SHERMAN POWER STG |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 326
148 | PANDA TEMPLE I POWER CTG1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
149 | PANDA TEMPLE I POWER CTG2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
150 | PANDA TEMPLE I POWER STG |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312
151 | PANDA TEMPLE II POWER CTG1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2
152 | PANDA TEMPLE II POWER CTG2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2
153 | PANDA TEMPLE II POWER STG |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7
154 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
155 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
156 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
157 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
158 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
159 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
160 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
161 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
162 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
163 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
164 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
165 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
166 | R MASSENGALE ST7 (LP&L) |  | R_MASSENGALE_7 | LUBBOCK | GAS | PANHANDLE | 1959 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
167 | R MASSENGALE GT8 (LP&L) |  | R_MASSENGALE_8 | LUBBOCK | GAS | PANHANDLE | 2000 | 0 | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
168 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
169 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
170 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
171 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323
172 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
173 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
174 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
175 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
176 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
177 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
178 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
179 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
180 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
181 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
182 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
183 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
184 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
185 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
186 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
187 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
188 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
189 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
190 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
191 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
192 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
193 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6
194 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
195 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
196 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
197 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
198 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
199 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
200 | WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
201 | WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
202 | WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 272 | 272 | 272 | 272 | 272 | 272 | 272 | 272 | 272 | 272
203 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5
204 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5
205 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
206 | WOLF HOLLOW 2 CT5 |  | WHCCS2_CT4 | HOOD | GAS | NORTH | 2017 | 314.1 | 314.1 | 314.1 | 314.1 | 314.1 | 314.1 | 314.1 | 314.1 | 314.1 | 314.1
207 | WOLF HOLLOW 2 CT6 |  | WHCCS2_CT5 | HOOD | GAS | NORTH | 2017 | 317.9 | 317.9 | 317.9 | 317.9 | 317.9 | 317.9 | 317.9 | 317.9 | 317.9 | 317.9
208 | WOLF HOLLOW 2 STG6 |  | WHCCS2_STG6 | HOOD | GAS | NORTH | 2017 | 432 | 432 | 432 | 432 | 432 | 432 | 432 | 432 | 432 | 432
209 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
210 | BRANDON GT1 (LP&L) |  | BRANDON | LUBBOCK | GAS | PANHANDLE | 1990 | 0 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
211 | CASTLEMAN CHAMON 1 |  | CHAMON_CTG_0101 | HARRIS | GAS | HOUSTON | 2017 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
212 | CASTLEMAN CHAMON 2 |  | CHAMON_CTG_0301 | HARRIS | GAS | HOUSTON | 2017 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
213 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
214 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
215 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
216 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
217 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
218 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
219 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
220 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
221 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
222 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
223 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
224 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
225 | ELK STATION CTG 3 |  | AEEC_ELK_3 | HALE | GAS | PANHANDLE | 2016 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
226 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
227 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
228 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
229 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
230 | FRIENDSWOOD G |  | FEGC_UNIT1 | HARRIS | GAS | HOUSTON | 2018 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
231 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
232 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
233 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
234 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
235 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
236 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
237 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
238 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
239 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
240 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1
241 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3
242 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
243 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
244 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
245 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
246 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
247 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
248 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
249 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
250 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
251 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
252 | DENTON ENERGY CENTER A |  | DEC_AGR_A | DENTON | GAS | NORTH | 2018 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
253 | DENTON ENERGY CENTER B |  | DEC_AGR_B | DENTON | GAS | NORTH | 2018 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
254 | DENTON ENERGY CENTER C |  | DEC_AGR_C | DENTON | GAS | NORTH | 2018 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
255 | DENTON ENERGY CENTER D |  | DEC_AGR_D | DENTON | GAS | NORTH | 2018 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
256 | PEARSALL IC ENGINE PLANT A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
257 | PEARSALL IC ENGINE PLANT B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
258 | PEARSALL IC ENGINE PLANT C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
259 | PEARSALL IC ENGINE PLANT D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
260 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
261 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
262 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
263 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
264 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
265 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS | GALVESTON | 2018 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
266 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS | HOUSTON | 2018 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
267 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS | HOUSTON | 2018 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
268 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS | HOUSTON | 2018 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
269 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS | HOUSTON | 2018 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
270 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS | HOUSTON | 2018 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
271 | REDGATE A |  | REDGATE_AGR_A | HIDALGO | GAS | SOUTH | 2016 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
272 | REDGATE B |  | REDGATE_AGR_B | HIDALGO | GAS | SOUTH | 2016 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
273 | REDGATE C |  | REDGATE_AGR_C | HIDALGO | GAS | SOUTH | 2016 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
274 | REDGATE D |  | REDGATE_AGR_D | HIDALGO | GAS | SOUTH | 2016 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
275 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
276 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
277 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
278 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
279 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
280 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
281 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
282 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
283 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
284 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
285 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
286 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
287 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
288 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
289 | SKY GLOBAL POWER ONE A |  | SKY1_SKY1A | COLORADO | GAS | SOUTH | 2016 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
290 | SKY GLOBAL POWER ONE B |  | SKY1_SKY1B | COLORADO | GAS | SOUTH | 2016 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
291 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
292 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
293 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
294 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
295 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
296 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
297 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
298 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
299 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
300 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
301 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
302 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
303 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
304 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
305 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
306 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
307 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
308 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
309 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745
310 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
311 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
312 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
313 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
314 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
315 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
316 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395
317 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
318 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
319 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
320 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523
321 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
322 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
323 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568
324 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
325 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410
326 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
327 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5
328 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5
329 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
330 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
331 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
332 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
333 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
334 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
335 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
336 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
337 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336
338 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
339 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
340 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
341 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217
342 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
343 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412
344 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
345 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
346 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
347 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 527 | 527 | 527 | 527 | 527 | 527 | 527 | 527 | 527 | 527
348 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
349 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
350 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
351 | FORT WORTH METHANE LFG |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
352 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
353 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
354 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
355 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
356 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
357 | VIRIDIS ENERGY-ALVIN LFG |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
358 | VIRIDIS ENERGY-HUMBLE LFG |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
359 | VIRIDIS ENERGY-LIBERTY LFG |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
360 | VIRIDIS ENERGY-TRINITY BAY LFG |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
361 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
362 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
363 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
364 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
365 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
366 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
367 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 65323.3 | 65323.3 | 65400.3 | 65400.3 | 65400.3 | 65400.3 | 65400.3 | 65400.3 | 65400.3 | 65400.3
368
369 | Operational Resources (Hydro)
370 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
371 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
372 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
373 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
374 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
375 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
376 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
377 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
378 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
379 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
380 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
381 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
382 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
383 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
384 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
385 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
386 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
387 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
388 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
389 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
390 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
391 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
392 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
393 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
394 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
395 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
396 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
397 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
398 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
399 | Operational Capacity Total (Hydro) | [6 empty] | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1
400 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 463.4748 | 463.4748 | 463.4748 | 463.4748 | 463.4748 | 463.4748 | 463.4748 | 463.4748 | 463.4748 | 463.4748
401
402 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
403 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 65421.7748 | 65786.7748 | 65863.7748 | 65863.7748 | 65863.7748 | 65863.7748 | 65863.7748 | 65863.7748 | 65863.7748 | 65863.7748
404
405 | Operational Resources (Switchable)
406 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS | PANHANDLE | 2016 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
407 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS | PANHANDLE | 2016 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
408 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS | PANHANDLE | 2016 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
409 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS | PANHANDLE | 2016 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
410 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS | PANHANDLE | 2016 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
411 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
412 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
413 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
414 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
415 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
416 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
417 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
418 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
419 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
420 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
421 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
422 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
423 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
424 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402
425 | Switchable Capacity Total | [6 empty] | 3515.8 | 3515.8 | 3515.8 | 3515.8 | 3515.8 | 3515.8 | 3515.8 | 3515.8 | 3515.8 | 3515.8
426
427 | Switchable Capacity Unavailable to ERCOT
428 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6
429 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6
430 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | 0 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6 | -54.6
431 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190
432 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190
433 | TENASKA FRONTIER STATION |  | FTR_FTR_UNAVAIL | FANNIN | GAS | NORTH | 2016 | -300 | -300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
434 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  |  |  |  | -789.2 | -843.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8
435
436 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 118 | 118 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0
437
438 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 3475.9495 | 3475.9495 | 3475.9495 | 3475.9495 | 3475.9495 | 3475.9495 | 3475.9495 | 3475.9495 | 3475.9495 | 3475.9495
439 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | -151 | -187 | -216 | -156 | -156 | -166 | -166 | -166 | -166 | -166
440
441 | Operational Resources (Wind)
442 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
443 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
444 | BLUE SUMMIT WIND 5 |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
445 | BLUE SUMMIT WIND 6 |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
446 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2013 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
447 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND | PANHANDLE | 2015 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8
448 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND | NORTH | 2017 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9
449 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND | NORTH | 2017 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7
450 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
451 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
452 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
453 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
454 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
455 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
456 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
457 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
458 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
459 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5
460 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
461 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
462 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
463 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
464 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
465 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
466 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD COUNTY | WIND | PANHANDLE | 2017 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
467 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND | WEST | 2017 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
468 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND | WEST | 2017 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
469 | DESERT SKY WIND 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
470 | DESERT SKY WIND 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5
471 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND | PANHANDLE | 2016 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
472 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND | PANHANDLE | 2016 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
473 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7
474 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND | WEST | 2017 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
475 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND | WEST | 2017 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
476 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND | PANHANDLE | 2017 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2
477 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND | NORTH | 2018 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
478 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND | WEST | 2017 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8
479 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND | WEST | 2017 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6
480 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2
481 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
482 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
483 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
484 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4
485 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
486 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
487 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
488 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND | WEST | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
489 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND | WEST | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
490 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND | WEST | 2016 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9
491 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
492 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND | PANHANDLE | 2015 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9
493 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
494 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REGAN AND IRION | WIND | WEST | 2018 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
495 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REGAN AND IRION | WIND | WEST | 2018 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5
496 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND | SOUTH | 2016 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
497 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND | SOUTH | 2016 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
498 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND | SOUTH | 2016 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
499 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND | WEST | 2017 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
500 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND | WEST | 2017 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
501 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6
502 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
503 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5
504 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
505 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
506 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND | WEST | 2008 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
507 | INDIAN MESA WIND |  | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
508 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND | SOUTH | 2015 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
509 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND | SOUTH | 2015 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
510 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND | SOUTH | 2017 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
511 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND | SOUTH | 2017 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
512 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND | SOUTH | 2017 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
513 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2
514 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
515 | KEECHI WIND 138 KV JOPLIN |  | KEECHI_U1 | JACK | WIND | NORTH | 2015 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
516 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
517 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
518 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
519 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
520 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
521 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND | NORTH | 2015 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3
522 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND | NORTH | 2015 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
523 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
524 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
525 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
526 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
527 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
528 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2010 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
529 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2010 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
530 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
531 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
532 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND | SOUTH | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
533 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND | SOUTH | 2016 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
534 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND | SOUTH | 2016 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
535 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND | PANHANDLE | 2017 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
536 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND | PANHANDLE | 2017 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
537 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
538 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
539 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
540 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
541 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
542 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND | WEST | 2018 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
543 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
544 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
545 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8
546 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD COUNTY | WIND | PANHANDLE | 2017 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
547 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
548 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
549 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
550 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
551 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
552 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
553 | PANTHER CREEK WIND 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
554 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
555 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
556 | PYRON WIND 1 |  | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
557 | PYRON WIND 2 |  | PYR_PYRON2 | SCURRY AND FISHER | WIND | WEST | 2008 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5
558 | RATTLESNAKE DEN WIND PHASE 1 G1 |  | RSNAKE_G1 | GLASSCOCK | WIND | WEST | 2015 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3
559 | RATTLESNAKE DEN WIND PHASE 1 G2 |  | RSNAKE_G2 | GLASSCOCK | WIND | WEST | 2015 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
560 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
561 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND | WEST | 2017 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
562 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND | WEST | 2017 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4
563 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
564 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND | WEST | 2008 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
565 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND | PANHANDLE | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
566 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND | SOUTH | 2018 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
567 | SALT FORK 1 WIND 1 |  | SALTFORK_UNIT1 | DONLEY | WIND | PANHANDLE | 2017 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
568 | SALT FORK 1 WIND 2 |  | SALTFORK_UNIT2 | DONLEY | WIND | PANHANDLE | 2017 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
569 | SAND BLUFF WIND |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
570 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND | SOUTH | 2015 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
571 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
572 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND | WEST | 2015 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1
573 | SHERBINO 1 WIND |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
574 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
575 | SILVER STAR WIND |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
576 | SNYDER WIND |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
577 | SOUTH PLAINS WIND I |  | SPLAIN1_WIND1 | FLOYD | WIND | PANHANDLE | 2015 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
578 | SOUTH PLAINS WIND 2 |  | SPLAIN1_WIND2 | FLOYD | WIND | PANHANDLE | 2015 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
579 | SOUTH PLAINS WIND II A |  | SPLAIN2_WIND21 | FLOYD | WIND | PANHANDLE | 2016 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
580 | SOUTH PLAINS WIND II B |  | SPLAIN2_WIND22 | FLOYD | WIND | PANHANDLE | 2016 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8
581 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2
582 | SPINNING SPUR WIND TWO |  | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
583 | SPINNING SPUR 3 [WIND 1] |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND | PANHANDLE | 2015 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
584 | SPINNING SPUR 3 [WIND 2] |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND | PANHANDLE | 2015 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
585 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
586 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2
587 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND | WEST | 2015 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7
588 | SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
589 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
590 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8
591 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
592 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
593 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
594 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
595 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
596 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
597 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
598 | TRENT WIND |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
599 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5
600 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
601 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
602 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND | NORTH | 2017 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6
603 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND | PANHANDLE | 2016 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9
604 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND | PANHANDLE | 2016 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3
605 | WEST TEXAS WIND |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3
606 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
607 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3
608 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6
609 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
610 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND | WEST | 2017 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
611 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND | WEST | 2017 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
612 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
613 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
614 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | bar: 2019 to 2028
615 | Operational Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8
616 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
617
618 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
619 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
620 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
621 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
622 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
623 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
624 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4
625 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
626 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
627 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
628 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
629 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
630 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5
631 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9
632 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
633 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
634 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
635 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
636 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2
637 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
638 | Operational Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6
639 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
640
641 | Operational Wind Capacity Total (All Counties) |  | WIND_OPERATIONAL |  |  |  |  | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4
642
643 | Operational Resources (Solar)
644 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
645 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
646 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
647 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
648 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
649 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1
650 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2
651 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
652 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
653 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2
654 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4
655 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
656 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
657 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
658 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
659 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
660 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
661 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | bar: 2019 to 2028
662 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
663 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
664 | FIFTH GENERATION SOLAR 1 |  | DG_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
665 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
666 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
667 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
668 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
669 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
670 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
671 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
672 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
673 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
674 | Operational Capacity Total (Solar) | [6 empty] | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4
675 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
676
677 | Operational Resources (Storage)
678 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
679 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
680 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
681 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
682 | OCI ALAMO 1 |  | DG_OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | bar: 2019 to 2028
683 | TOS BATTERY STORAGE |  | DG_TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
684 | Operational Capacity Total (Storage) | [6 empty] | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5
685 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
686
687 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
688
689 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
690
691 | Non-Synchronous Tie Resources
692 | EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
693 | NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
694 | EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
695 | LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
696 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
697 | SHARYLAND RAILROAD TIE 2 |  | DC_R2 | HIDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
698 | Non-Synchronous Ties Total | [6 empty] | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250
699 | Non-Synchronous Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 429.6 | 429.6 | 429.6 | 429.6 | 429.6 | 429.6 | 429.6 | 429.6 | 429.6 | 429.6
700
701 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
702 | FGE TEXAS I PROJECT | 16INR0010 |  | MITCHELL | GAS | WEST | 2021 | 0 | 0 | 742.9 | 742.9 | 742.9 | 742.9 | 742.9 | 742.9 | 742.9 | 742.9
703 | HALYARD HENDERSON | 16INR0045 |  | HENDERSON | GAS | NORTH | 2021 | 0 | 0 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484
704 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS | SOUTH | 2021 | 0 | 0 | 397.8 | 397.8 | 397.8 | 397.8 | 397.8 | 397.8 | 397.8 | 397.8
705 | HUDSON (BRAZORIA ENERGY G) | 16INR0076 |  | BRAZORIA | GAS | COASTAL | 2019 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
706 | MIRAGE | 17INR0022 |  | HARRIS | GAS | HOUSTON | 2019 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
707 | VICTORIA CITY (CITYVICT) | 18INR0035 |  | REFUGIO | GAS | COASTAL | 2019 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
708 | VICTORIA PORT (VICTPORT) | 17INR0045 |  | CALHOUN | GAS | COASTAL | 2019 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
709 | Planned Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 301 | 301 | 1925.7 | 1925.7 | 1925.7 | 1925.7 | 1925.7 | 1925.7 | 1925.7 | 1925.7
710
711 | Planned Wind Resources with Executed SGIA
712 | ARMSTRONG WIND | 18INR0029 |  | ARMSTRONG | WIND | PANHANDLE | 2020 | 0 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253
713 | BARROW RANCH (JUMBO HILL WIND) | 18INR0038 |  | ANDREWS | WIND | WEST | 2019 | 0 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
714 | BLUE SUMMIT II | 18INR0070 |  | WILBARGER | WIND | WEST | 2019 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
715 | CABEZON WIND (RIO BRAVO I WIND) | 17INR0005 |  | STARR | WIND | SOUTH | 2019 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6
716 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND | WEST | 2018 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4
717 | CANADIAN BREAKS WIND | 13INR0026 |  | OLDHAM | WIND | PANHANDLE | 2019 | 0 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
718 | CANYON WIND | 18INR0030 |  | SCURRY | WIND | WEST | 2020 | 0 | 0 | 300.9 | 300.9 | 300.9 | 300.9 | 300.9 | 300.9 | 300.9 | 300.9
719 | COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2019 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
720 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND | WEST | 2019 | 0 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5
721 | DARMSTADT | 18INR0023 |  | SCHLEICHER | WIND | WEST | 2019 | 0 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9
722 | EASTER WIND | 15INR0063 |  | CASTRO | WIND | PANHANDLE | 2020 | 0 | 0 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5
723 | EDMONDSON RANCH WIND | 18INR0043 |  | GLASSCOCK | WIND | WEST | 2020 | 0 | 0 | 292.5 | 292.5 | 292.5 | 292.5 | 292.5 | 292.5 | 292.5 | 292.5
724 | FOARD CITY WIND | 19INR0019 |  | FOARD | WIND | WEST | 2019 | 0 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
725 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND | PANHANDLE | 2019 | 0 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8
726 | GOPHER CREEK WIND | 18INR0067 |  | SCURRY | WIND | WEST | 2019 | 0 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
727 | HARALD (BEARKAT WIND B) | 15INR0064b |  | GLASSCOCK | WIND | WEST | 2019 | 0 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
728 | HART WIND | 16INR0033 |  | CASTRO | WIND | PANHANDLE | 2020 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
729 | HIGH LONESOME W | 19INR0038 |  | CROCKETT | WIND | WEST | 2019 | 0 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5
730 | KONTIKI 1 WIND | 19INR0099a |  | GLASSCOCK | WIND | WEST | 2019 | 0 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3
731 | KONTIKI 2 WIND | 19INR0099b |  | GLASSCOCK | WIND | WEST | 2020 | 0 | 0 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3
732 | LOCKETT WIND FARM | 16INR0062b |  | WILBARGER | WIND | WEST | 2019 | 0 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
733 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND | SOUTH | 2019 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
734 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND | WEST | 2018 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
735 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2018 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
736 | MAVERICK CREEK I | 20INR0045 |  | CONCHO | WIND | WEST | 2020 | 0 | 0 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252
737 | MAVERICK CREEK II | 20INR0046 |  | CONCHO | WIND | WEST | 2020 | 0 | 0 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252
738 | MESTENO WIND | 16INR0081 |  | STARR | WIND | SOUTH | 2019 | 0 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
739 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND | PANHANDLE | 2019 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
740 | OVEJA WIND | 18INR0033 |  | IRION | WIND | WEST | 2019 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
741 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2020 | 0 | 0 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
742 | PRAIRIE HILL WIND | 19INR0100 |  | LIMESTONE | WIND | NORTH | 2020 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
743 | PUMPKIN FARM WIND | 16INR0037c |  | FLOYD | WIND | PANHANDLE | 2019 | 0 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9
744 | RANCHERO WIND | 20INR0011 |  | CROCKETT | WIND | WEST | 2019 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
745 | RTS 2 WIND (HEART OF TEXAS WIND) | 18INR0016 |  | MCCULLOCH | WIND | SOUTH | 2019 | 0 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8
746 | S_HILLS WIND (LITTLE MOUNTAIN WIND) | 12INR0055 |  | BAYLOR | WIND | WEST | 2019 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
747 | SAGE DRAW WIND | 19INR0163 |  | LYNN | WIND | WEST | 2019 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
748 | SCANDIA WIND DEF | 13INR0010def |  | PARMER | WIND | PANHANDLE | 2019 | 0 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3
749 | SILVER CANYON WIND A | 12INR0002a |  | BRISCOE | WIND | PANHANDLE | 2020 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
750 | TAHOKA WIND (STAKED PLAINS WIND 1) | 18INR0025 |  | LYNN | WIND | WEST | 2019 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
751 | TG EAST WIND | 19INR0052 |  | KNOX | WIND | WEST | 2019 | 0 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6
752 | TORRECILLAS WIND | 14INR0045 |  | WEBB | WIND | SOUTH | 2018 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5
753 | VERA WIND | 19INR0051 |  | KNOX | WIND | WEST | 2019 | 0 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8
754 | WILDROSE WIND (SWISHER WIND) | 13INR0038 |  | SWISHER | WIND | PANHANDLE | 2020 | 0 | 0 | 302.5 | 302.5 | 302.5 | 302.5 | 302.5 | 302.5 | 302.5 | 302.5
755 | WILSON RANCH (INFINITY LIVE OAK WIND) | 12INR0060 |  | SCHLEICHER | WIND | WEST | 2019 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
756 | WKN AMADEUS WIND | 14INR0009 |  | KENT | WIND | WEST | 2019 | 0 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9
757 | CHALUPA WIND | 20INR0042 |  | CAMERON | WIND-C | COASTAL | 2020 | 0 | 0 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
758 | CRANEL WIND | 19INR0112 |  | REFUGIO | WIND-C | COASTAL | 2019 | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
759 | KARANKAWA 2 WIND FARM | 19INR0074 |  | SAN PATRICIO | WIND-C | COASTAL | 2019 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
760 | KARANKAWA WIND ALT A | 18INR0014 |  | SAN PATRICIO | WIND-C | COASTAL | 2019 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
761 | LAS MAJADAS WIND | 17INR0035 |  | WILLACY | WIND-C | COASTAL | 2020 | 0 | 0 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8
762 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | COASTAL | 2018 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9
763 | PALMAS ALTAS WIND | 17INR0037 |  | CAMERON | WIND-C | COASTAL | 2019 | 0 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9
764 | SHAFFER (PATRIOT WIND/PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2019 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226
765 | PEYTON CREEK WIND | 18INR0018 |  | MATAGORDA | WIND-C | COASTAL | 2019 | 0 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
766 | RAYMOND WIND | 18INR0059 |  | WILLACY | WIND-C | COASTAL | 2019 | 0 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
767 | STELLA 1 WIND | 15INR0035 |  | KENEDY | WIND-C | COASTAL | 2018 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201
768 | Planned Capacity Total (Wind) | [6 empty] | 2160.6 | 10477.3 | 13484.8 | 13484.8 | 13484.8 | 13484.8 | 13484.8 | 13484.8 | 13484.8 | 13484.8
769
770 | Planned Wind Capacity Sub-total (Non-Coastal Counties) |  | WIND_PLANNED_NC |  |  |  |  | 1570.7 | 8769.7 | 11330.4 | 11330.4 | 11330.4 | 11330.4 | 11330.4 | 11330.4 | 11330.4 | 11330.4
771 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PL_PEAK_PCT_NC | % |  |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
772
773 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 589.9 | 1707.6 | 2154.4 | 2154.4 | 2154.4 | 2154.4 | 2154.4 | 2154.4 | 2154.4 | 2154.4
774 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
775
776 | Planned Solar Resources with Executed SGIA
777 | ARAGORN SOLAR | 19INR0088 |  | CULBERSON | SOLAR | WEST | 2020 | 0 | 0 | 186.3 | 186.3 | 186.3 | 186.3 | 186.3 | 186.3 | 186.3 | 186.3
778 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) | 16INR0019 |  | COKE | SOLAR | WEST | 2018 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
779 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 |  | PECOS | SOLAR | WEST | 2019 | 0 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
780 | FS BARILLA SOLAR 1B [HOVEY_UNIT2] | 12INR0059b |  | PECOS | SOLAR | WEST | 2019 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
781 | HOLSTEIN SOLAR | 19INR0009 |  | NOLAN | SOLAR | WEST | 2020 | 0 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
782 | LAMESA SOLAR (PHASE II) | 16INR0023b |  | DAWSON | SOLAR | WEST | 2018 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
783 | LONG DRAW SOLAR | 18INR0055 |  | BORDEN | SOLAR | WEST | 2020 | 0 | 0 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
784 | MISAE SOLAR | 18INR0045 |  | CHILDRESS | SOLAR | PANHANDLE | 2019 | 0 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8
785 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2020 | 0 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201
786 | OBERON SOLAR | 19INR0083 |  | ECTOR | SOLAR | WEST | 2019 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
787 | PFLUGERVILLE SOLAR | 15INR0090 |  | TRAVIS | SOLAR | SOUTH | 2019 | 0 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
788 | PHOEBE SOLAR | 19INR0029 |  | WINKLER | SOLAR | WEST | 2019 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
789 | PROSPERO SOLAR | 19INR0092 |  | ANDREWS | SOLAR | WEST | 2019 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
790 | QUEEN SOLAR | 19INR0102 |  | UPTON | SOLAR | WEST | 2019 | 0 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
791 | RAMBLER SOLAR | 19INR0114 |  | TOM GREEN | SOLAR | WEST | 2019 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
792 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2019 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
793 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2019 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
794 | RE MAPLEWOOD 2C SOLAR | 17INR0020c |  | PECOS | SOLAR | WEST | 2019 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
795 | RE MAPLEWOOD 2D SOLAR | 17INR0020d |  | PECOS | SOLAR | WEST | 2020 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
796 | RE MAPLEWOOD 2E SOLAR | 17INR0020e |  | PECOS | SOLAR | WEST | 2020 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
797 | SODA LAKE SOLAR 1 | 18INR0040 |  | CRANE | SOLAR | WEST | 2020 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
798 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2020 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
799 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2019 | 0 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
800 | WAYMARK SOLAR | 16INR0115 |  | PECOS | SOLAR | WEST | 2018 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
801 | WEST OF PECOS SOLAR | 14INR0044 |  | REEVES | SOLAR | WEST | 2019 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
802 | WINKLER SOLAR (RES WINK SOLAR) | 18INR0022 |  | WINKLER | SOLAR | WEST | 2019 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
803 | Planned Capacity Total (Solar) | [6 empty] | 269.4 | 3099.2 | 4110.5 | 4110.5 | 4110.5 | 4110.5 | 4110.5 | 4110.5 | 4110.5 | 4110.5
804 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
805
806 | Planned Storage Resources with Executed SGIA
807 | Planned Capacity Total (Storage) | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
808 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809
810 | Seasonal Mothballed Resources
811 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
812 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
813 | Total Seasonal Mothballed Capacity | [6 empty] | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
814
815 | Mothballed Resources
816 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
817 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
818 | S R BERTRON U1 (SINCE 5/15/2013) |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
819 | S R BERTRON U2 (SINCE 5/15/2013) |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
820 | Total Mothballed Capacity | [6 empty] | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120
821
822 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
823 | Total Retiring Capacity | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes:
Capacity changes due to planned repower projects are reflected in the operational units' ratings upon project completion.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational capacity formula.
These resources are assumed to provide regulation reserves rather than sustained capacity available to meet peak loads.

## SummerFuelTypes
Summer Fuel Types - ERCOT
Fuel type is based on the primary fuel. Capacity contribution of the wind resources is included at 15% for Non-Coastal and 58% for Coastal counties, while the solar capacity contribution is 74%. Private Use Network, Hydro and Non-Synchronous Tie resources are included based on the three-year average historical capability for each Summer Season's 20 peak load hours. Non-Synchronous Tie resources are categorized as Other. Mothballed resource capacity is excluded except for Available Mothball Capacity based on a Seasonal Availability Schedule or Owner's reported Return Probability. Private Use Network is categorized as gas.
In MW
Fuel_Type | Capacity_Pct | 2019 | 2020 | 2021 | 2022 | 2023
Biomass | 100% | 201.7 | 201.7 | 201.7 | 201.7 | 201.7
Coal | 100% | 14768 | 14768 | 14768 | 14650 | 14650
Gas | 100% | 51864.1495 | 51773.5495 | 53746.2495 | 53806.2495 | 53806.2495
Nuclear | 100% | 4960 | 4960 | 4960 | 4960 | 4960
Other | 100% | 429.6 | 429.6 | 429.6 | 429.6 | 429.6
Hydro | 83.49% | 463.4748 | 463.4748 | 463.4748 | 463.4748 | 463.4748
Wind | 15% | 3072.975 | 4152.825 | 4536.93 | 4536.93 | 4536.93
Wind-C | 58% | 1861.51 | 2509.776 | 2768.92 | 2768.92 | 2768.92
Solar | 74% | 1298.552 | 3392.604 | 4140.966 | 4140.966 | 4140.966
Storage | 0% | 0 | 0 | 0 | 0 | 0
Total |  | 78919.9613 | 82651.5293 | 86015.8403 | 85957.8403 | 85957.8403
In Percentages
Fuel_Type |  | 2019 | 2020 | 2021 | 2022 | 2023
Biomass |  | 0.2556% | 0.244% | 0.2345% | 0.2346% | 0.2346%
Coal |  | 18.71% | 17.87% | 17.17% | 17.04% | 17.04%
Natural Gas |  | 65.72% | 62.64% | 62.48% | 62.6% | 62.6%
Nuclear |  | 6.285% | 6.001% | 5.766% | 5.77% | 5.77%
Other |  | 0.5443% | 0.5198% | 0.4994% | 0.4998% | 0.4998%
Hydro |  | 0.5873% | 0.5608% | 0.5388% | 0.5392% | 0.5392%
Wind |  | 3.894% | 5.024% | 5.275% | 5.278% | 5.278%
Wind-C |  | 2.359% | 3.037% | 3.219% | 3.221% | 3.221%
Solar |  | 1.645% | 4.105% | 4.814% | 4.817% | 4.817%
Storage |  | 0% | 0% | 0% | 0% | 0%
Total |  | 100% | 100% | 100% | 100% | 100%

## WinterSummary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Winter Summary: 2018/2019 through 2022/2023
Load Forecast, MW: |  | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023
| Winter Peak Demand (based on normal weather) | 58196.0718 | 61149.762 | 62782.2869 | 64448.5253 | 65966.9584
| plus: Energy Efficiency Program Savings Forecast | 1543.7865 | 1822.0386 | 2103.9244 | 2389.4438 | 2678.597
| Total Winter Peak Demand (before Reductions from Energy Efficiency Programs) | 59739.8583 | 62971.8006 | 64886.2113 | 66837.9692 | 68645.5554
| less: Load Resources providing Responsive Reserves | -1317.126 | -1317.126 | -1317.126 | -1317.126 | -1317.126
| less: Load Resources providing Non-Spinning Reserves | 0 | 0 | 0 | 0 | 0
| less: Emergency Response Service (10- and 30-min ramp products) | -958.0044 | -952.9962 | -952.9962 | -952.9962 | -952.9962
| less: TDSP Standard Offer Load Management Programs | 0 | 0 | 0 | 0 | 0
| less: Energy Efficiency Program Savings Forecast | -1543.7865 | -1822.0386 | -2103.9244 | -2389.4438 | -2678.597
| Firm Peak Load, MW | 55920.9414 | 58879.6398 | 60512.1647 | 62178.4031 | 63696.8362
Resources, MW: |  | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023
| Installed Capacity, Thermal/Hydro | 68275.2644 | 68745.2644 | 69136.2644 | 69217.7644 | 69217.7644
| Switchable Generation Resource Capacity, MW | 3736 | 3736 | 3736 | 3736 | 3736
| less: Switchable Capacity Unavailable to ERCOT | -802 | -858 | -858 | -558 | -558
| Available Mothballed Capacity | 0 | 0 | 0 | 0 | 0
| Capacity from Private Use Networks | 3305.2321 | 3269.2321 | 3240.2321 | 3300.2321 | 3300.2321
| Non-Coastal Wind, Peak Average Capacity Contribution (20%) | 3783.16 | 3783.16 | 3783.16 | 3783.16 | 3783.16
| Coastal Wind, Peak Average Capacity Contribution (43%) | 1126.428 | 1126.428 | 1126.428 | 1126.428 | 1126.428
| Solar Utility-Scale, Peak Average Capacity Contribution (12%) | 178.248 | 178.248 | 178.248 | 178.248 | 178.248
| Storage, Peak Average Capacity Contribution (0%) | 0 | 0 | 0 | 0 | 0
| RMR Capacity to be under Contract | 0 | 0 | 0 | 0 | 0
| Capacity Pending Retirement, MW | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, MW | 79602.3324 | 79980.3324 | 80342.3324 | 80783.8324 | 80783.8324
| Capacity Contribution - Non-Synchronous Ties | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812
| Planned Resources (not wind or solar) with Signed IA, Air Permits and Water Rights | 0 | 307 | 307 | 1931.7 | 1931.7
| Planned Non-Coastal Wind with Signed IA, Peak Average Capacity Contribution (20%) | 0 | 1363.58 | 2187.4 | 2277.9 | 2277.9
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution (43%) | 0 | 380.98 | 851.572 | 926.392 | 926.392
| Planned Solar Utility-Scale, Peak Average Capacity Contribution (12%) | 0 | 200.424 | 445.26 | 493.26 | 493.26
| Planned Storage, Peak Average Capacity Contribution (0%) | 0 | 0 | 0 | 0 | 0
| Total Capacity, MW | 79888.9137 | 82518.8977 | 84420.1457 | 86699.6657 | 86699.6657
| Reserve Margin | 42.86% | 40.15% | 39.51% | 39.44% | 36.11%
(Total Resources - Firm Load Forecast) / Firm Load Forecast

## WinterCapacities
Unit Capacities - Winter
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449
12 | GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 0 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470
13 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
14 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785
15 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824
16 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836
17 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815
18 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
19 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
20 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840
21 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825
22 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
23 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
24 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950
25 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
26 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
27 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664
28 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663
29 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
30 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
31 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
32 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
33 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
34 | BARNEY M DAVIS REPOWER CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
35 | BARNEY M DAVIS REPOWER CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
36 | BARNEY M DAVIS REPOWER STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
40 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9
41 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2
42 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9
43 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5
44 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7
45 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
46 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
47 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
48 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
49 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
50 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
51 | CALHOUN (PORT COMFORT) 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS | COASTAL | 2017 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
52 | CALHOUN (PORT COMFORT) 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS | COASTAL | 2017 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
53 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
54 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
55 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
56 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
57 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
58 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
59 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
60 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
61 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
62 | COLORADO BEND II CT7 |  | CBECII_CT7 | WHARTON | GAS | SOUTH | 2017 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
63 | COLORADO BEND II CT8 |  | CBECII_CT8 | WHARTON | GAS | SOUTH | 2017 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
64 | COLORADO BEND II ST8 |  | CBECII_STG9 | WHARTON | GAS | SOUTH | 2017 | 498 | 498 | 498 | 498 | 498 | 498 | 498 | 498 | 498 | 498 | 498
65 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
66 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
67 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
68 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
69 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
70 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
71 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
72 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
73 | DEER PARK ENERGY CENTER STG |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
74 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
75 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245
76 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
77 | FERGUSON REPLACEMENT CTG1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
78 | FERGUSON REPLACEMENT CTG2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
79 | FERGUSON REPLACEMENT STG |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
80 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
81 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
82 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
83 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
84 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
85 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
86 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418
87 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418
88 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7
89 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7
90 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8
91 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
92 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
93 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7
94 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS | COASTAL | 2000 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
95 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS | COASTAL | 2000 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
96 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS | COASTAL | 2000 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
97 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
98 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
99 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
100 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
101 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
102 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
103 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
104 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
105 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242
106 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243
107 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
108 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
109 | HIDALGO ENERGY CENTER STG |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
110 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2006 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
111 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2006 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
112 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2006 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293
113 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
114 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
115 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310
116 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
117 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
118 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
119 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
120 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
121 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
122 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
123 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
124 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
125 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
126 | LOST PINES POWER STG |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192
127 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6
128 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6
129 | MAGIC VALLEY STATION STG |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9
130 | MIDLOTHIAN ENERGY FACILITY CS 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258
131 | MIDLOTHIAN ENERGY FACILITY CS 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256
132 | MIDLOTHIAN ENERGY FACILITY CS 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
133 | MIDLOTHIAN ENERGY FACILITY CS 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258
134 | MIDLOTHIAN ENERGY FACILITY CS 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276
135 | MIDLOTHIAN ENERGY FACILITY CS 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278
136 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
137 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
138 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325
139 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9
140 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 151.5 | 151.5 | 151.5 | 151.5 | 151.5 | 151.5 | 151.5 | 151.5 | 151.5 | 151.5 | 151.5
141 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
142 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
143 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212
144 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212
145 | PANDA SHERMAN POWER CTG1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
146 | PANDA SHERMAN POWER CTG2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
147 | PANDA SHERMAN POWER STG |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
148 | PANDA TEMPLE I POWER CTG1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
149 | PANDA TEMPLE I POWER CTG2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
150 | PANDA TEMPLE I POWER STG |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
151 | PANDA TEMPLE II POWER CTG1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
152 | PANDA TEMPLE II POWER CTG2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
153 | PANDA TEMPLE II POWER STG |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
154 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
155 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
156 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
157 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
158 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
159 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
160 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
161 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
162 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
163 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
164 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
165 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
166 | R MASSENGALE ST7 (LP&L) |  | R_MASSENGALE_7 | LUBBOCK | GAS | PANHANDLE | 1959 | 0 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
167 | R MASSENGALE GT8 (LP&L) |  | R_MASSENGALE_8 | LUBBOCK | GAS | PANHANDLE | 2000 | 0 | 0 | 0 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
168 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
169 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
170 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
171 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323
172 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
173 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
174 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
175 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
176 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
177 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
178 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
179 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
180 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
181 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
182 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
183 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
184 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
185 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
186 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
187 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
188 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
189 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
190 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
191 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
192 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
193 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5
194 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
195 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
196 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
197 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
198 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
199 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
200 | WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 251 | 251 | 251 | 251 | 251 | 251 | 251 | 251 | 251 | 251 | 251
201 | WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256
202 | WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298
203 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
204 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
205 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293
206 | WOLF HOLLOW 2 CT5 |  | WHCCS2_CT4 | HOOD | GAS | NORTH | 2017 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335
207 | WOLF HOLLOW 2 CT6 |  | WHCCS2_CT5 | HOOD | GAS | NORTH | 2017 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335
208 | WOLF HOLLOW 2 STG6 |  | WHCCS2_STG6 | HOOD | GAS | NORTH | 2017 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 460
209 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
210 | BRANDON GT1 (LP&L) |  | BRANDON | LUBBOCK | GAS | PANHANDLE | 1990 | 0 | 0 | 0 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5
211 | CASTLEMAN CHAMON 1 |  | CHAMON_CTG_0101 | HARRIS | GAS | HOUSTON | 2017 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
212 | CASTLEMAN CHAMON 2 |  | CHAMON_CTG_0301 | HARRIS | GAS | HOUSTON | 2017 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
213 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
214 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
215 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
216 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
217 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
218 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
219 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
220 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
221 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
222 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
223 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4
224 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4
225 | ELK STATION CTG 3 |  | AEEC_ELK_3 | HALE | GAS | PANHANDLE | 2016 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
226 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
227 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
228 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
229 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
230 | FRIENDSWOOD G |  | FEGC_UNIT1 | HARRIS | GAS | HOUSTON | 2018 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
231 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
232 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
233 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
234 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
235 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
236 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
237 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
238 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
239 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
240 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4
241 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4
242 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
243 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
244 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
245 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
246 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
247 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
248 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
249 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
250 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
251 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
252 | DENTON ENERGY CENTER A |  | DEC_AGR_A | DENTON | GAS | NORTH | 2018 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
253 | DENTON ENERGY CENTER B |  | DEC_AGR_B | DENTON | GAS | NORTH | 2018 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
254 | DENTON ENERGY CENTER C |  | DEC_AGR_C | DENTON | GAS | NORTH | 2018 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
255 | DENTON ENERGY CENTER D |  | DEC_AGR_D | DENTON | GAS | NORTH | 2018 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
256 | PEARSALL IC ENGINE PLANT A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
257 | PEARSALL IC ENGINE PLANT B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
258 | PEARSALL IC ENGINE PLANT C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
259 | PEARSALL IC ENGINE PLANT D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
260 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
261 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
262 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
263 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
264 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
265 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
266 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
267 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
268 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
269 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS | HOUSTON | 2018 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
270 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
271 | REDGATE A |  | REDGATE_AGR_A | HIDALGO | GAS | SOUTH | 2016 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
272 | REDGATE B |  | REDGATE_AGR_B | HIDALGO | GAS | SOUTH | 2016 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
273 | REDGATE C |  | REDGATE_AGR_C | HIDALGO | GAS | SOUTH | 2016 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
274 | REDGATE D |  | REDGATE_AGR_D | HIDALGO | GAS | SOUTH | 2016 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
275 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
276 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
277 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
278 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
279 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
280 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
281 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
282 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
283 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
284 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
285 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
286 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
287 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
288 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
289 | SKY GLOBAL POWER ONE A |  | SKY1_SKY1A | COLORADO | GAS | SOUTH | 2016 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
290 | SKY GLOBAL POWER ONE B |  | SKY1_SKY1B | COLORADO | GAS | SOUTH | 2016 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
291 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
292 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
293 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
294 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
295 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
296 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
297 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
298 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
299 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
300 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
301 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
302 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
303 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
304 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
305 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
306 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
307 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
308 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330
309 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745
310 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
311 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
312 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
313 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428
314 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
315 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
316 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395
317 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
318 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
319 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
320 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523
321 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
322 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
323 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568
324 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
325 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410
326 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
327 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5
328 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5
329 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
330 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
331 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
332 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
333 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
334 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
335 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
336 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
337 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340
338 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
339 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
340 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
341 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217
342 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
343 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412
344 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
345 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
346 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258
347 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552
348 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
349 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
350 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
351 | FORT WORTH METHANE LFG |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
352 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
353 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
354 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
355 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
356 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
357 | VIRIDIS ENERGY-ALVIN LFG |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
358 | VIRIDIS ENERGY-HUMBLE LFG |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
359 | VIRIDIS ENERGY-LIBERTY LFG |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
360 | VIRIDIS ENERGY-TRINITY BAY LFG |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
361 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
362 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
363 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
364 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
365 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
366 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
367 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 68209.2 | 68679.2 | 68679.2 | 68760.7 | 68760.7 | 68760.7 | 68760.7 | 68760.7 | 68760.7 | 68760.7 | 68760.7
368
369 | Operational Resources (Hydro)
370 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
371 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
372 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
373 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
374 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
375 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
376 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
377 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
378 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
379 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
380 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
381 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
382 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
383 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
384 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
385 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
386 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
387 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
388 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
389 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
390 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
391 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
392 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
393 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
394 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
395 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
396 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
397 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
398 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
399 | Operational Capacity Total (Hydro) | [6 empty] | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1 | 555.1
400 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 457.0644 | 457.0644 | 457.0644 | 457.0644 | 457.0644 | 457.0644 | 457.0644 | 457.0644 | 457.0644 | 457.0644 | 457.0644
401
402 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -391 | -391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
403 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 68275.2644 | 68745.2644 | 69136.2644 | 69217.7644 | 69217.7644 | 69217.7644 | 69217.7644 | 69217.7644 | 69217.7644 | 69217.7644 | 69217.7644
404
405 | Operational Resources (Switchable)
406 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS | PANHANDLE | 2016 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
407 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS | PANHANDLE | 2016 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
408 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS | PANHANDLE | 2016 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
409 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS | PANHANDLE | 2016 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
410 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS | PANHANDLE | 2016 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
411 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
412 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
413 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307
414 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
415 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
416 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307
417 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
418 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
419 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
420 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
421 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
422 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179
423 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
424 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
425 | Switchable Capacity Total | [6 empty] | 3736 | 3736 | 3736 | 3736 | 3736 | 3736 | 3736 | 3736 | 3736 | 3736 | 3736
426
427 | Switchable Capacity Unavailable to ERCOT
428 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56
429 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56
430 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | 0 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56
431 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195
432 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195
433 | TENASKA FRONTIER STATION |  | FTR_FTR_UNAVAIL | FANNIN | GAS | NORTH | 2016 | -300 | -300 | -300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
434 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  |  |  |  | -802 | -858 | -858 | -558 | -558 | -558 | -558 | -558 | -558 | -558 | -558
435
436 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
437
438 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 3456.2321 | 3456.2321 | 3456.2321 | 3456.2321 | 3456.2321 | 3456.2321 | 3456.2321 | 3456.2321 | 3456.2321 | 3456.2321 | 3456.2321
439 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | -151 | -187 | -216 | -156 | -156 | -166 | -166 | -166 | -166 | -166 | -166
440
441 | Operational Resources (Wind)
442 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
443 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
444 | BLUE SUMMIT WIND 5 |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
445 | BLUE SUMMIT WIND 6 |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
446 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2013 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
447 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND | PANHANDLE | 2015 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8
448 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND | NORTH | 2017 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9
449 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND | NORTH | 2017 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7
450 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
451 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
452 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
453 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
454 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
455 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
456 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
457 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
458 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
459 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5
460 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
461 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
462 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
463 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
464 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
465 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
466 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD COUNTY | WIND | PANHANDLE | 2017 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
467 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND | WEST | 2017 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
468 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND | WEST | 2017 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
469 | DESERT SKY WIND 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
470 | DESERT SKY WIND 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5
471 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND | PANHANDLE | 2016 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
472 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND | PANHANDLE | 2016 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
473 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7
474 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND | WEST | 2017 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
475 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND | WEST | 2017 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
476 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND | PANHANDLE | 2017 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2
477 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND | NORTH | 2018 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
478 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND | WEST | 2017 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8
479 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND | WEST | 2017 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6
480 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2
481 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
482 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
483 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
484 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4
485 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
486 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
487 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
488 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND | WEST | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
489 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND | WEST | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
490 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND | WEST | 2016 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9
491 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
492 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND | PANHANDLE | 2015 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9
493 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
494 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REGAN AND IRION | WIND | WEST | 2018 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
495 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REGAN AND IRION | WIND | WEST | 2018 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5
496 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND | SOUTH | 2016 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
497 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND | SOUTH | 2016 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
498 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND | SOUTH | 2016 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
499 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND | WEST | 2017 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
500 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND | WEST | 2017 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
501 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6 | 206.6
502 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
503 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5
504 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
505 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
506 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND | WEST | 2008 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
507 | INDIAN MESA WIND |  | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
508 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND | SOUTH | 2015 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
509 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND | SOUTH | 2015 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
510 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND | SOUTH | 2017 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
511 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND | SOUTH | 2017 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
512 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND | SOUTH | 2017 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
513 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2
514 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
515 | KEECHI WIND 138 KV JOPLIN |  | KEECHI_U1 | JACK | WIND | NORTH | 2015 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
516 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
517 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
518 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
519 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
520 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
521 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND | NORTH | 2015 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3
522 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND | NORTH | 2015 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
523 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
524 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
525 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
526 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
527 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
528 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2010 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
529 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2010 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
530 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
531 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
532 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND | SOUTH | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
533 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND | SOUTH | 2016 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
534 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND | SOUTH | 2016 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
535 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND | PANHANDLE | 2017 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
536 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND | PANHANDLE | 2017 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
537 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
538 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
539 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
540 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
541 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
542 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND | WEST | 2018 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
543 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
544 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
545 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8
546 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD COUNTY | WIND | PANHANDLE | 2017 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
547 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
548 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
549 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
550 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
551 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
552 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
553 | PANTHER CREEK WIND 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
554 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
555 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
556 | PYRON WIND 1 |  | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
557 | PYRON WIND 2 |  | PYR_PYRON2 | SCURRY AND FISHER | WIND | WEST | 2008 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5
558 | RATTLESNAKE DEN WIND PHASE 1 G1 |  | RSNAKE_G1 | GLASSCOCK | WIND | WEST | 2015 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3
559 | RATTLESNAKE DEN WIND PHASE 1 G2 |  | RSNAKE_G2 | GLASSCOCK | WIND | WEST | 2015 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
560 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
561 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND | WEST | 2017 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
562 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND | WEST | 2017 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4
563 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
564 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND | WEST | 2008 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
565 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND | PANHANDLE | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
566 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND | SOUTH | 2018 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
567 | SALT FORK 1 WIND 1 |  | SALTFORK_UNIT1 | DONLEY | WIND | PANHANDLE | 2017 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
568 | SALT FORK 1 WIND 2 |  | SALTFORK_UNIT2 | DONLEY | WIND | PANHANDLE | 2017 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
569 | SAND BLUFF WIND |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
570 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND | SOUTH | 2015 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
571 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
572 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND | WEST | 2015 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1
573 | SHERBINO 1 WIND |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
574 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
575 | SILVER STAR WIND |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
576 | SNYDER WIND |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
577 | SOUTH PLAINS WIND I |  | SPLAIN1_WIND1 | FLOYD | WIND | PANHANDLE | 2015 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
578 | SOUTH PLAINS WIND 2 |  | SPLAIN1_WIND2 | FLOYD | WIND | PANHANDLE | 2015 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
579 | SOUTH PLAINS WIND II A |  | SPLAIN2_WIND21 | FLOYD | WIND | PANHANDLE | 2016 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
580 | SOUTH PLAINS WIND II B |  | SPLAIN2_WIND22 | FLOYD | WIND | PANHANDLE | 2016 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8
581 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2
582 | SPINNING SPUR WIND TWO |  | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
583 | SPINNING SPUR 3 [WIND 1] |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND | PANHANDLE | 2015 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
584 | SPINNING SPUR 3 [WIND 2] |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND | PANHANDLE | 2015 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
585 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
586 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2
587 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND | WEST | 2015 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7
588 | SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
589 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
590 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8 | 98.8
591 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
592 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
593 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
594 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
595 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
596 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
597 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
598 | TRENT WIND |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
599 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5
600 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
601 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
602 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND | NORTH | 2017 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6
603 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND | PANHANDLE | 2016 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9
604 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND | PANHANDLE | 2016 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3
605 | WEST TEXAS WIND |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3
606 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
607 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3
608 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6
609 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
610 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND | WEST | 2017 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
611 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND | WEST | 2017 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
612 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
613 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
614 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
615 | Operational Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8 | 18915.8
616 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
617
618 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
619 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
620 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
621 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
622 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
623 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
624 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4
625 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
626 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
627 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
628 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
629 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
630 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5
631 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9
632 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
633 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
634 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
635 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
636 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2
637 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
638 | Operational Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6 | 2619.6
639 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
640
641 | Operational Wind Capacity Total (All Counties) |  | WIND_OPERATIONAL |  |  |  |  | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4 | 21535.4
642
643 | Operational Resources (Solar)
644 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
645 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
646 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
647 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
648 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
649 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1
650 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2
651 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
652 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
653 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2
654 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4 | 106.4
655 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
656 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
657 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
658 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
659 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
660 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
661 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
662 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
663 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
664 | FIFTH GENERATION SOLAR 1 |  | DG_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
665 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
666 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
667 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
668 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
669 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
670 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
671 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
672 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
673 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
674 | Operational Capacity Total (Solar) | [6 empty] | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4 | 1485.4
675 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
676
677 | Operational Resources (Storage)
678 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
679 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
680 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
681 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
682 | OCI ALAMO 1 |  | DG_OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
683 | TOS BATTERY STORAGE |  | DG_TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
684 | Operational Capacity Total (Storage) | [6 empty] | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5 | 86.5
685 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
686
687 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
688
689 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
690
691 | Non-Synchronous Tie Resources
692 | EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
693 | NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
694 | EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
695 | LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
696 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
697 | SHARYLAND RAILROAD TIE 2 |  | DC_R2 | HIDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
698 | Non-Synchronous Ties Total | [6 empty] | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250
699 | Non-Synchronous Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812
700
701 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
702 | FGE TEXAS I PROJECT | 16INR0010 |  | MITCHELL | GAS | WEST | 2021 | 0 | 0 | 0 | 742.9 | 742.9 | 742.9 | 742.9 | 742.9 | 742.9 | 742.9 | 742.9
703 | HALYARD HENDERSON | 16INR0045 |  | HENDERSON | GAS | NORTH | 2021 | 0 | 0 | 0 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484
704 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS | SOUTH | 2021 | 0 | 0 | 0 | 397.8 | 397.8 | 397.8 | 397.8 | 397.8 | 397.8 | 397.8 | 397.8
705 | HUDSON (BRAZORIA ENERGY G) | 16INR0076 |  | BRAZORIA | GAS | COASTAL | 2019 | 0 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
706 | MIRAGE | 17INR0022 |  | HARRIS | GAS | HOUSTON | 2019 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
707 | VICTORIA CITY (CITYVICT) | 18INR0035 |  | REFUGIO | GAS | COASTAL | 2019 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
708 | VICTORIA PORT (VICTPORT) | 17INR0045 |  | CALHOUN | GAS | COASTAL | 2019 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
709 | Planned Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 0 | 307 | 307 | 1931.7 | 1931.7 | 1931.7 | 1931.7 | 1931.7 | 1931.7 | 1931.7 | 1931.7
710
711 | Planned Wind Resources with Executed SGIA
712 | ARMSTRONG WIND | 18INR0029 |  | ARMSTRONG | WIND | PANHANDLE | 2020 | 0 | 0 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 253
713 | BARROW RANCH (JUMBO HILL WIND) | 18INR0038 |  | ANDREWS | WIND | WEST | 2019 | 0 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
714 | BLUE SUMMIT II | 18INR0070 |  | WILBARGER | WIND | WEST | 2019 | 0 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
715 | CABEZON WIND (RIO BRAVO I WIND) | 17INR0005 |  | STARR | WIND | SOUTH | 2019 | 0 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6 | 237.6
716 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND | WEST | 2018 | 0 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4
717 | CANADIAN BREAKS WIND | 13INR0026 |  | OLDHAM | WIND | PANHANDLE | 2019 | 0 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
718 | CANYON WIND | 18INR0030 |  | SCURRY | WIND | WEST | 2020 | 0 | 0 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360
719 | COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2019 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
720 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND | WEST | 2019 | 0 | 0 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5 | 242.5
721 | DARMSTADT | 18INR0023 |  | SCHLEICHER | WIND | WEST | 2019 | 0 | 0 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9
722 | EASTER WIND | 15INR0063 |  | CASTRO | WIND | PANHANDLE | 2020 | 0 | 0 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5
723 | EDMONDSON RANCH WIND | 18INR0043 |  | GLASSCOCK | WIND | WEST | 2020 | 0 | 0 | 292.5 | 292.5 | 292.5 | 292.5 | 292.5 | 292.5 | 292.5 | 292.5 | 292.5
724 | FOARD CITY WIND | 19INR0019 |  | FOARD | WIND | WEST | 2019 | 0 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
725 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND | PANHANDLE | 2019 | 0 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8 | 496.8
726 | GOPHER CREEK WIND | 18INR0067 |  | SCURRY | WIND | WEST | 2019 | 0 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
727 | HARALD (BEARKAT WIND B) | 15INR0064b |  | GLASSCOCK | WIND | WEST | 2019 | 0 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
728 | HART WIND | 16INR0033 |  | CASTRO | WIND | PANHANDLE | 2020 | 0 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
729 | HIGH LONESOME W | 19INR0038 |  | CROCKETT | WIND | WEST | 2019 | 0 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5
730 | KONTIKI 1 WIND | 19INR0099a |  | GLASSCOCK | WIND | WEST | 2019 | 0 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3
731 | KONTIKI 2 WIND | 19INR0099b |  | GLASSCOCK | WIND | WEST | 2020 | 0 | 0 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3
732 | LOCKETT WIND FARM | 16INR0062b |  | WILBARGER | WIND | WEST | 2019 | 0 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
733 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND | SOUTH | 2019 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
734 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND | WEST | 2018 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
735 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2018 | 0 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
736 | MAVERICK CREEK I | 20INR0045 |  | CONCHO | WIND | WEST | 2020 | 0 | 0 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252
737 | MAVERICK CREEK II | 20INR0046 |  | CONCHO | WIND | WEST | 2020 | 0 | 0 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252
738 | MESTENO WIND | 16INR0081 |  | STARR | WIND | SOUTH | 2019 | 0 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
739 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND | PANHANDLE | 2019 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
740 | OVEJA WIND | 18INR0033 |  | IRION | WIND | WEST | 2019 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
741 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2020 | 0 | 0 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
742 | PRAIRIE HILL WIND | 19INR0100 |  | LIMESTONE | WIND | NORTH | 2020 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
743 | PUMPKIN FARM WIND | 16INR0037c |  | FLOYD | WIND | PANHANDLE | 2019 | 0 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9 | 280.9
744 | RANCHERO WIND | 20INR0011 |  | CROCKETT | WIND | WEST | 2019 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
745 | RTS 2 WIND (HEART OF TEXAS WIND) | 18INR0016 |  | MCCULLOCH | WIND | SOUTH | 2019 | 0 | 0 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8
746 | S_HILLS WIND (LITTLE MOUNTAIN WIND) | 12INR0055 |  | BAYLOR | WIND | WEST | 2019 | 0 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
747 | SAGE DRAW WIND | 19INR0163 |  | LYNN | WIND | WEST | 2019 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
748 | SCANDIA WIND DEF | 13INR0010def |  | PARMER | WIND | PANHANDLE | 2019 | 0 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3 | 600.3
749 | SILVER CANYON WIND A | 12INR0002a |  | BRISCOE | WIND | PANHANDLE | 2020 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
750 | TAHOKA WIND (STAKED PLAINS WIND 1) | 18INR0025 |  | LYNN | WIND | WEST | 2019 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
751 | TG EAST WIND | 19INR0052 |  | KNOX | WIND | WEST | 2019 | 0 | 0 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6 | 275.6
752 | TORRECILLAS WIND | 14INR0045 |  | WEBB | WIND | SOUTH | 2018 | 0 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5 | 300.5
753 | VERA WIND | 19INR0051 |  | KNOX | WIND | WEST | 2019 | 0 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8
754 | WILDROSE WIND (SWISHER WIND) | 13INR0038 |  | SWISHER | WIND | PANHANDLE | 2020 | 0 | 0 | 0 | 302.5 | 302.5 | 302.5 | 302.5 | 302.5 | 302.5 | 302.5 | 302.5
755 | WILSON RANCH (INFINITY LIVE OAK WIND) | 12INR0060 |  | SCHLEICHER | WIND | WEST | 2019 | 0 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
756 | WKN AMADEUS WIND | 14INR0009 |  | KENT | WIND | WEST | 2019 | 0 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9 | 245.9
757 | CHALUPA WIND | 20INR0042 |  | CAMERON | WIND-C | COASTAL | 2020 | 0 | 0 | 0 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
758 | CRANEL WIND | 19INR0112 |  | REFUGIO | WIND-C | COASTAL | 2019 | 0 | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
759 | KARANKAWA 2 WIND FARM | 19INR0074 |  | SAN PATRICIO | WIND-C | COASTAL | 2019 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
760 | KARANKAWA WIND ALT A | 18INR0014 |  | SAN PATRICIO | WIND-C | COASTAL | 2019 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
761 | LAS MAJADAS WIND | 17INR0035 |  | WILLACY | WIND-C | COASTAL | 2020 | 0 | 0 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8
762 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | COASTAL | 2018 | 0 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9
763 | PALMAS ALTAS WIND | 17INR0037 |  | CAMERON | WIND-C | COASTAL | 2019 | 0 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9
764 | SHAFFER (PATRIOT WIND/PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2019 | 0 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226
765 | PEYTON CREEK WIND | 18INR0018 |  | MATAGORDA | WIND-C | COASTAL | 2019 | 0 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
766 | RAYMOND WIND | 18INR0059 |  | WILLACY | WIND-C | COASTAL | 2019 | 0 | 0 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
767 | STELLA 1 WIND | 15INR0035 |  | KENEDY | WIND-C | COASTAL | 2018 | 0 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201
768 | Planned Capacity Total (Wind) | [6 empty] | 0 | 7703.9 | 12917.4 | 13543.9 | 13543.9 | 13543.9 | 13543.9 | 13543.9 | 13543.9 | 13543.9 | 13543.9
769
770 | Planned Wind Capacity Sub-total (Non-Coastal Counties) |  | WIND_PLANNED_NC |  |  |  |  | 0 | 6817.9 | 10937 | 11389.5 | 11389.5 | 11389.5 | 11389.5 | 11389.5 | 11389.5 | 11389.5 | 11389.5
771 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PL_PEAK_PCT_NC | % |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
772
773 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 0 | 886 | 1980.4 | 2154.4 | 2154.4 | 2154.4 | 2154.4 | 2154.4 | 2154.4 | 2154.4 | 2154.4
774 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
775
776 | Planned Solar Resources with Executed SGIA
777 | ARAGORN SOLAR | 19INR0088 |  | CULBERSON | SOLAR | WEST | 2020 | 0 | 0 | 186.3 | 186.3 | 186.3 | 186.3 | 186.3 | 186.3 | 186.3 | 186.3 | 186.3
778 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) | 16INR0019 |  | COKE | SOLAR | WEST | 2018 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
779 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 |  | PECOS | SOLAR | WEST | 2019 | 0 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
780 | FS BARILLA SOLAR 1B [HOVEY_UNIT2] | 12INR0059b |  | PECOS | SOLAR | WEST | 2019 | 0 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
781 | HOLSTEIN SOLAR | 19INR0009 |  | NOLAN | SOLAR | WEST | 2020 | 0 | 0 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
782 | LAMESA SOLAR (PHASE II) | 16INR0023b |  | DAWSON | SOLAR | WEST | 2018 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
783 | LONG DRAW SOLAR | 18INR0055 |  | BORDEN | SOLAR | WEST | 2020 | 0 | 0 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
784 | MISAE SOLAR | 18INR0045 |  | CHILDRESS | SOLAR | PANHANDLE | 2019 | 0 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8 | 240.8
785 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2020 | 0 | 0 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201
786 | OBERON SOLAR | 19INR0083 |  | ECTOR | SOLAR | WEST | 2019 | 0 | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
787 | PFLUGERVILLE SOLAR | 15INR0090 |  | TRAVIS | SOLAR | SOUTH | 2019 | 0 | 0 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
788 | PHOEBE SOLAR | 19INR0029 |  | WINKLER | SOLAR | WEST | 2019 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
789 | PROSPERO SOLAR | 19INR0092 |  | ANDREWS | SOLAR | WEST | 2019 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
790 | QUEEN SOLAR | 19INR0102 |  | UPTON | SOLAR | WEST | 2019 | 0 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
791 | RAMBLER SOLAR | 19INR0114 |  | TOM GREEN | SOLAR | WEST | 2019 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
792 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2019 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
793 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2019 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
794 | RE MAPLEWOOD 2C SOLAR | 17INR0020c |  | PECOS | SOLAR | WEST | 2019 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
795 | RE MAPLEWOOD 2D SOLAR | 17INR0020d |  | PECOS | SOLAR | WEST | 2020 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
796 | RE MAPLEWOOD 2E SOLAR | 17INR0020e |  | PECOS | SOLAR | WEST | 2020 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
797 | SODA LAKE SOLAR 1 | 18INR0040 |  | CRANE | SOLAR | WEST | 2020 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
798 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2020 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
799 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2019 | 0 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
800 | WAYMARK SOLAR | 16INR0115 |  | PECOS | SOLAR | WEST | 2018 | 0 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
801 | WEST OF PECOS SOLAR | 14INR0044 |  | REEVES | SOLAR | WEST | 2019 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
802 | WINKLER SOLAR (RES WINK SOLAR) | 18INR0022 |  | WINKLER | SOLAR | WEST | 2019 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
803 | Planned Capacity Total (Solar) | [6 empty] | 0 | 1670.2 | 3710.5 | 4110.5 | 4110.5 | 4110.5 | 4110.5 | 4110.5 | 4110.5 | 4110.5 | 4110.5
804 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
805
806 | Planned Storage Resources with Executed SGIA
807 | Planned Capacity Total (Storage) | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
808 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809
810 | Seasonal Mothballed Resources
811 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
812 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
813 | Total Seasonal Mothballed Capacity | [6 empty] | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
814
815 | Mothballed Resources
816 | GIBBONS CREEK U1 (OCT 2018 TO MID-MAY/JUN 2019) |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
817 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430
818 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
819 | S R BERTRON U1 (SINCE 5/15/2013) |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
820 | S R BERTRON U2 (SINCE 5/15/2013) |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
821 | Total Mothballed Capacity | [6 empty] | 1612 | 1142 | 1142 | 1142 | 1142 | 1142 | 1142 | 1142 | 1142 | 1142 | 1142
822
823 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
824 | Total Retiring Capacity | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes:
Capacity changes due to planned repower projects are reflected in the operational units' ratings upon project completion.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational capacity formula.
These resources are assumed to provide regulation reserves rather than sustained capacity available to meet peak loads.

## WinterFuelTypes
Winter Fuel Types - ERCOT
Fuel type is based on the primary fuel. Capacity contribution of the wind resources is included at 20% for Non-Coastal and 43% for Coastal counties, while the solar capacity contribution is 12%. Private Use Network, Hydro and Non-Synchronous Tie resources are included based on the three-year average historical capability for each Summer Season's 20 peak load hours. Non-Synchronous Tie resources are categorized as Other. Mothballed resource capacity is excluded except for Available Mothball Capacity based on a Seasonal Availability Schedule or Owner's reported Return Probability. Private Use Network is categorized as gas.
In MW
Fuel_Type | Capacity_Pct | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023
Biomass | 100% | 201.7 | 201.7 | 201.7 | 201.7 | 201.7
Coal | 100% | 14252 | 14722 | 14722 | 14722 | 14722
Gas | 100% | 54854.7321 | 55069.7321 | 55040.7321 | 57106.9321 | 57106.9321
Nuclear | 100% | 5140 | 5140 | 5140 | 5140 | 5140
Other | 100% | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812
Hydro | 82.34% | 457.0644 | 457.0644 | 457.0644 | 457.0644 | 457.0644
Wind | 20% | 3783.16 | 5146.74 | 5970.56 | 6061.06 | 6061.06
Wind-C | 43% | 1126.428 | 1507.408 | 1978 | 2052.82 | 2052.82
Solar | 12% | 178.248 | 378.672 | 623.508 | 671.508 | 671.508
Storage | 0% | 0 | 0 | 0 | 0 | 0
Total |  | 80279.9137 | 82909.8977 | 84420.1457 | 86699.6657 | 86699.6657
In Percentages
Fuel_Type |  | 2018/2019 | 2019/2020 | 2020/2021 | 2021/2022 | 2022/2023
Biomass |  | 0.2512% | 0.2433% | 0.2389% | 0.2326% | 0.2326%
Coal |  | 17.75% | 17.76% | 17.44% | 16.98% | 16.98%
Gas |  | 68.33% | 66.42% | 65.2% | 65.87% | 65.87%
Nuclear |  | 6.403% | 6.2% | 6.089% | 5.929% | 5.929%
Other |  | 0.357% | 0.3457% | 0.3395% | 0.3305% | 0.3305%
Hydro |  | 0.5693% | 0.5513% | 0.5414% | 0.5272% | 0.5272%
Wind |  | 4.712% | 6.208% | 7.072% | 6.991% | 6.991%
Wind-C |  | 1.403% | 1.818% | 2.343% | 2.368% | 2.368%
Solar |  | 0.222% | 0.4567% | 0.7386% | 0.7745% | 0.7745%
Storage |  | 0% | 0% | 0% | 0% | 0%
Total |  | 100% | 100% | 100% | 100% | 100%

## Supplemental
Capacity of Proposed Generation Resources Based on Interconnection Milestone Status
Cumulative Summer Capacity Contribution (in MW) of Resources Available by June 1 of the Reporting Year
| 2019 | 2020 | 2021 | 2022 | 2023
Planned Resource Category
Commissioning Plan Submitted | 521.667 | 521.667 | 521.667 | 521.667 | 521.667
Planning Guide 6.9 Criteria plus completed Full Interconnect Study | 895.974 | 1820.852 | 1820.852 | 1820.852 | 1820.852
Meets Planning Guide Sec. 6.9 Criteria (CDR plus TSP Financial Security Posted and Notice to Proceed) | 918.849 | 2727.967 | 3227.057 | 3227.057 | 3227.057
CDR Eligible (signed IA, air permits, proof of adequate water supply) | 1078.109 | 4900.277 | 7916.588 | 7916.588 | 7916.588
Signed Interconnection Agreement with the TSP | 1078.109 | 4900.277 | 7916.588 | 8659.488 | 8659.488
Full Interconnect Study Requested | 1208.109 | 12328.2615 | 24866.9791 | 27745.0581 | 28041.0581
__________________________________________________
Notes: (1) Resource categories are listed by highest to lowest likelihood that the resource capacity will be in commercial operation in the reported year. For example, resources in the Commissioning Plan Submitted category have reached the "substantially completed construction" phase, and associated transmission switchyard facilities are operational. Conversely, resources in the Full Interconnection Study Requested category include projects that are generally in the development proposal stage and have a significant risk of interconnection request cancellation or project development delays. (2) The data presented here is based upon the latest information provided to ERCOT by resource developers and can change without notice. (3) Resource developers may execute an Interconnection Agreement with a TSP prior to completion of the Full Interconnection Study. This is most common with wind and solar projects. (4) Wind and solar resource capacities reflect their estimated summer on-peak average values as determined by the methodologies in Protocol section 3.2.6.2.2. (5) Battery storage projects are assumed to provide no seasonal sustained peak-hour capacity contributions, and are thus reported as zero MW.
Capacity, Demand and Reserves, 2024 Through Winter 2027/2028
The summer and winter capacity summaries below show the reserve margin impact of not adding any new resources during the latter half of the CDR forecast period. Since project developers typically submit interconnection requests no more than three to five years before the facility is expected to enter commercial operations, reserve margins reported beyond this window always show a declining trend. Also note that the reserve margin impact of potential future unit retirements and mothballing, and associated market responses to replace retired units, are not accounted for here or elsewhere in this CDR report.
Summer
Load Forecast, MW: | 2024 | 2025 | 2026 | 2027 | 2028
Summer Peak Demand (based on normal weather) | 83716.46 | 85327.0628 | 86940.3083 | 88507.6439 | 90020.6994
plus: Energy Efficiency Program Savings Forecast, per Utilities Code Section 39.905 (b-4) | 2973.5438 | 3272.1243 | 3577.3074 | 3889.7949 | 4177.1981
Total Summer Peak Demand (before Reductions from Energy Efficiency Programs) | 86690.0038 | 88599.187 | 90517.6156 | 92397.4388 | 94197.8975
less: Load Resources providing Responsive Reserves | -1125.06 | -1125.06 | -1125.06 | -1125.06 | -1125.06
less: Load Resources providing Non-Spinning Reserves | 0 | 0 | 0 | 0 | 0
less: Emergency Response Service (10- and 30-min ramp products) | -753.0048 | -753.0048 | -753.0048 | -753.0048 | -753.0048
less: TDSP Standard Offer Load Management Programs | -281.5608 | -281.5608 | -281.5608 | -281.5608 | -281.5608
less Energy Efficiency Programs | -2973.5438 | -3272.1243 | -3577.3074 | -3889.7949 | -4177.1981
Firm Peak Load, MW | 81556.8344 | 83167.4372 | 84780.6827 | 86348.0183 | 87861.0738
Resources, MW: | 2024 | 2025 | 2026 | 2027 | 2028
Installed Capacity, Thermal/Hydro | 65863.7748 | 65863.7748 | 65863.7748 | 65863.7748 | 65863.7748
Switchable Capacity, MW | 3515.8 | 3515.8 | 3515.8 | 3515.8 | 3515.8
less: Switchable Capacity Unavailable to ERCOT, MW | -543.8 | -543.8 | -543.8 | -543.8 | -543.8
Available Mothballed Capacity, MW | 0 | 0 | 0 | 0 | 0
Capacity from Private Use Networks | 3309.9495 | 3309.9495 | 3309.9495 | 3309.9495 | 3309.9495
Non-Coastal Wind, Peak Average Capacity Contribution (15%) | 2837.37 | 2837.37 | 2837.37 | 2837.37 | 2837.37
Coastal Wind, Peak Average Capacity Contribution (58%) | 1519.368 | 1519.368 | 1519.368 | 1519.368 | 1519.368
Solar Utility-Scale, Peak Average Capacity Contribution (74%) | 1099.196 | 1099.196 | 1099.196 | 1099.196 | 1099.196
RMR Capacity to be under Contract | 0 | 0 | 0 | 0 | 0
Capacity Pending Retirement, MW | 0 | 0 | 0 | 0 | 0
Operational Generation Capacity, MW | 77601.6583 | 77601.6583 | 77601.6583 | 77601.6583 | 77601.6583
Capacity Contribution - Non-Synchronous Ties, MW | 429.6 | 429.6 | 429.6 | 429.6 | 429.6
Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 1925.7 | 1925.7 | 1925.7 | 1925.7 | 1925.7
Planned Non-Coastal Wind with Signed IA, Peak Average Capacity Contribution (15%) | 1699.56 | 1699.56 | 1699.56 | 1699.56 | 1699.56
Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution (58%) | 1249.552 | 1249.552 | 1249.552 | 1249.552 | 1249.552
Planned Solar Utility-Scale, Peak Average Capacity Contribution (74%) | 3041.77 | 3041.77 | 3041.77 | 3041.77 | 3041.77
Total Capacity, MW | 85947.8403 | 85947.8403 | 85947.8403 | 85947.8403 | 85947.8403
Reserve Margin | 5.384% | 3.343% | 1.377% | -0.4634% | -2.178%
(Total Resources - Firm Load Forecast) / Firm Load Forecast
Winter
Load Forecast, MW: | 2023/2024 | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028
Winter Peak Demand (based on normal weather) | 67490.605 | 69001.808 | 70544.1549 | 72071.6045 | 73546.4911
plus: Energy Efficiency Program Savings Forecast, per Utilities Code Section 39.905 (b-4) | 2973.5438 | 3272.1243 | 3577.3074 | 3889.7949 | 4177.1981
Total Winter Peak Demand (before Reductions from Energy Efficiency Programs) | 70464.1488 | 72273.9322 | 74121.4623 | 75961.3993 | 77723.6892
less: Load Resources providing Responsive Reserves | -1317.126 | -1317.126 | -1317.126 | -1317.126 | -1317.126
less: Load Resources providing Non-Spinning Reserves | 0 | 0 | 0 | 0 | 0
less: Emergency Response Service (10- and 30-min ramp products) | -952.9962 | -952.9962 | -952.9962 | -952.9962 | -952.9962
less: TDSP Standard Offer Load Management Programs | 0 | 0 | 0 | 0 | 0
less Energy Efficiency Programs | -2973.5438 | -3272.1243 | -3577.3074 | -3889.7949 | -4177.1981
Firm Peak Load, MW | 65220.4828 | 66731.6858 | 68274.0327 | 69801.4823 | 71276.3689
Resources, MW: | 2023/2024 | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028
Installed Capacity, Thermal/Hydro | 69217.7644 | 69217.7644 | 69217.7644 | 69217.7644 | 69217.7644
Switchable Capacity | 3736 | 3736 | 3736 | 3736 | 3736
less: Switchable Capacity Unavailable to ERCOT | -558 | -558 | -558 | -558 | -558
Available Mothballed Capacity | 0 | 0 | 0 | 0 | 0
Capacity from Private Use Networks | 3290.2321 | 3290.2321 | 3290.2321 | 3290.2321 | 3290.2321
Non-Coastal Wind, Peak Average Capacity Contribution (20%) | 3783.16 | 3783.16 | 3783.16 | 3783.16 | 3783.16
Coastal Wind, Peak Average Capacity Contribution (43%) | 1126.428 | 1126.428 | 1126.428 | 1126.428 | 1126.428
Solar Utility-Scale, Peak Average Capacity Contribution (12%) | 178.248 | 178.248 | 178.248 | 178.248 | 178.248
RMR Capacity to be under Contract | 0 | 0 | 0 | 0 | 0
Capacity Pending Retirement, MW | 0 | 0 | 0 | 0 | 0
Operational Generation Capacity, MW | 80773.8324 | 80773.8324 | 80773.8324 | 80773.8324 | 80773.8324
Capacity Contribution - Non-Synchronous Ties | 286.5812 | 286.5812 | 286.5812 | 286.5812 | 286.5812
Planned Resources (not wind or solar) with Signed IA, Air Permits and Water Rights | 1931.7 | 1931.7 | 1931.7 | 1931.7 | 1931.7
Planned Non-Coastal Wind with Signed IA, Peak Average Capacity Contribution (20%) | 2277.9 | 2277.9 | 2277.9 | 2277.9 | 2277.9
Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution (43%) | 926.392 | 926.392 | 926.392 | 926.392 | 926.392
Planned Solar Utility-Scale, Peak Average Capacity Contribution (12%) | 493.26 | 493.26 | 493.26 | 493.26 | 493.26
Total Capacity, MW | 86689.6657 | 86689.6657 | 86689.6657 | 86689.6657 | 86689.6657
Reserve Margin | 32.92% | 29.91% | 26.97% | 24.19% | 21.62%
(Total Resources - Firm Load Forecast) / Firm Load Forecast