## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Chad Mulholland, NRG
ROS
December 6th, 2018

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    2 FMEs in the month of October
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 11/9/18
  Open Session Topic Item: NOGRR Realignment Draft with NPRR863 with PDCWG input of suggested language changes. Further review of NOGRR will be needed.
  Open Session Topic Item: No discussion on Southern Cross DC Tie. Directive 9 discussion to start in January 2019.
  Only one item from BAL-001-TRE-01 September 2017 Workshop remains but interested PDCWG stakeholder has not attended meetings and discussion on topic has no other PDCWG stakeholder interest.
  Regulation & Frequency Control Reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 2 FMEs in October
  10/16/2018 20:15:26
    Loss of 475 MW
    Interconnection Frequency Response:
    7 of 47 Evaluated Generation Resources ( 2 of 23 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    7 of 47 Evaluated Generation Resources ( 1 of 23 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.
  10/19/2018 15:23:23
    Loss of 630 MW
    Interconnection Frequency Response:
    5 of 41 Evaluated Generation Resources ( 1 of 26 RRS Providers) had less than 75% of their expected Initial Primary Frequency Response.
    2 of 41 Evaluated Generation Resources ( 1 of 26 RRS Providers) had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 921.60 MW/0.1Hz

## Slide 7: Frequency Control Report
October 2018

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections

## Slide 12: ERCOT Total Energy

## Slide 13: ERCOT Total Energy from Wind Generation

## Slide 14: ERCOT % Energy from Wind Generation

## Slide 15
Questions?