## General S1
Commissioning Plan | [5 empty] | Where to find most of the information required for this tab in the RARF
[6 empty] | File | Tab | Title | Cell(s)
|  | Resource Name: | Generic Resource Name |  |  | GENERAL_SITE_ESIID_Information | General and Site Information | Resource Site Name | B16
|  | Resource Code: | GR |  |  | GENERAL_SITE_ESIID_Information | General and Site Information | Resource Site Code | B17
|  | Resource Entity Name: | Generic Resource (RE) |  |  | GENERAL_SITE_ESIID_Information | General and Site Information | Resource Entity Submitting Form | B12
|  | Resource QSE Name: | Generic Resource (QSE)
|  | Submittal Date: | 2015-01-26
|  | GINR Number | YYINRxxxx
Commissioning Plan Section 1: Resource Description
● | Fuel Category |  |  |  |  | Resource_Form_Pivoted | Unit Info | Fuel Information | N/A
● | Total Number of Units (Wind and Solar Resources Only) |  |  |  |  | Resource_Form_Pivoted | Turbine Details | Number of Turbine Manufacturer/Model | Column G
● | MW Capacity (sum of HRL) |  |  | 0 |  | Resource_Form_Pivoted | Parameters | High Reasonability Limit | Column C
● | Total Number of Loads |  |  |  |  | Transmission_Form_Pivoted | Load Data | Load Code | Column D
● | Capacity of the Modeled Loads |  |  | 0 | 0 | Transmission_Form_Pivoted | Load Data | Average Load / Average Mvar | Columns G & H
● | Total Number of Static Reactive Devices |  |  |  |  | Transmission_Form_Pivoted | Capacitor and Reactor Data | Capacitor Or Reactor | Column E
● | MVAr Capacity of Capacitor Banks |  |  | 0 |  | Transmission_Form_Pivoted | Capacitor and Reactor Data | Nominal Mvar | Column F
● | MVAr Capacity of Reactor Banks |  |  | 0 |  | Transmission_Form_Pivoted | Capacitor and Reactor Data | Nominal Mvar | Column F
● | County Location (list all that apply, use Notes if needed) |  |  |  |  | GENERAL_SITE_ESIID_Information | General and Site Information | County | B22
● | Point Of Interconnection (POI) Transmission Service Provider |  |  |  |  | Transmission_Form_Pivoted | Line Data | Line Voltage Level | Column N
● | POI Station Code (Mnemonic) |  |  |  |  | Transmission_Form_Pivoted | Line Data | ERCOT TO Station Code Mnemonic | Column L
● | POI Scheduled Voltage |  |  | 0 |  | Transmission_Form_Pivoted | Line Data | TSP Name | Column C
● | POI Segment Length (if applicable) |  |  | 0 |  | Transmission_Form_Pivoted | Line Data | Segment Length | Column K
● | Part 1 Notes:
Use this "Notes" area to describe your Reactive Devices or to describe your Combined-Cycle Configurations or to describe your Type of Wind Turbines/Solar Panels.
● | Status of required integration engineering studies for Generic Resource Name (Reactive Capability, Sub-synchronous Oscillation, and others as required by TSP and/or ERCOT).

## Controls S2
Commissioning Plan |  |  |  | Commissioning Plan
|  | Resource Name: | Generic Resource Name |  |  | Resource Name: | Generic Resource Name
Commissioning Plan Section 2 (Panel 1 of 2): Resource Controls |  |  |  | Commissioning Plan Section 2 (Panel 2 of 2): Resource Controls
● | Site Control System |  |  |  | ○ | Describe the availability of the AVR at Generic Resource Name. Include limitations of the AVR from initial synchronization through final commercial operations.
| ○ | Describe the Site Control System at Generic Resource Name.
Only Wind and Solar Resources are required to complete this box.
| ○ | Describe the availability of Site Control System at Generic Resource Name. Include limitations of the system from initial synchronization through Part 3 approval. |  |  | ○ | Describe the VSS/Reactive (Leading & Lagging) commissioning process at Generic Resource Name?
Only Wind and Solar Resources are required to complete this box.
● | Speed Control or Primary Frequency Response (PFR) |  |  | ● | Power System Stabilizers (PSS)
| ○ | Describe the PFR commissioning process at Generic Resource Name? |  |  | ○ | Describe the PSS commissioning process at Generic Resource Name?
|  | All resources must address both under-frequency and over-frequency capabilities. |  |  |  | Wind and Solar Resources are not required to complete this box
● | Voltage Control from the Automatic Voltage Regulator (AVR) |  |  | ● | Part 2 Notes:
| ○ | Describe the AVR commissioning process at Generic Resource Name?
Include voltage droop and deadband settings for your AVR.

## Shut-down & Telemetry S3-S4
Commissioning Plan
|  | Resource Name: | Generic Resource Name
|  | Resource Entity Name: | Generic Resource (RE)
|  | Resource QSE Name: | Generic Resource (QSE)
Commissioning Plan Section 3: Resource Shut-down Sequences
● | By completing and submitting to ERCOT this Commissioning Plan, Generic Resource Name and Generic Resource (QSE) acknowledge the requirement in the ERCOT Operating Guides, Section 2.2.10(4) that requires on-line Generation Resources to commence their shutdown sequence within five minutes of receipt of a Dispatch Instruction from ERCOT.
If, during the commissioning of Generic Resource Name, ERCOT provides an urgent Dispatch Instruction to reduce generation or remove the generator(s) from synchronization with ERCOT Transmission Grid, Generic Resource Name will accelerate the shutdown sequence and disconnection from the ERCOT Transmission Grid to comply with the time required in the Dispatch Instruction.
● | Orderly Shut-down at Generic Resource Name will be completed in |  |  | 0
● | Emergency Shut-down at Generic Resource Name will be completed in |  |  | 0
Commissioning Plan Section 4: Resource Telemetry Verification
● | Describe how Generic Resource (QSE) and Generic Resource (RE) will confirm telemetry quality (including validation, monitoring & troubleshooting) during the entire Commissioning Plan. Pages 19 & 20 of the Resource Interconnection Handbook has more telemetry information.
● | Telemetry contact information (2 preferred)

## Milestones S5
Commissioning Plan
| Resource Name: |  | Generic Resource Name
Replace the unit names with the actual Resource names from the RARF
Commissioning Plan Section 5: Resource Commissioning Milestones
[7 empty] | File | Tab | Title | Cell(s)
Commissioning Activity Dates (Planned) | Resource A | Resource B | Resource C | Resource D | Resource E | Resource F | Resource_Form_Pivoted | Unit Info | Resource Name (Unit Code/Mnemonic) | Column B
Model Ready Date
Site telemetry quality verification completed
Checklist Part 1 submitted
Proposed Resource Energization
Checklist Part 2 submitted
Proposed Resource Synchronization
PFR in-service
AVR in-service
VSS in-service
PSS in-service
Static Reactive Devices in-service
Plant Control System (MW & MVAr output controls) in-service Only 20 MVA can be electrically energized to the ERCOT grid until Control System is in-service
IRRs Only: Control capability verified for greater than 20 MVA operations
PFR testing for Part 3 requirements
AVR testing for Part 3 requirements
Lead reactive capability testing for Part 3 requirements
Lag reactive capability testing for Part 3 requirements
Checklist Part 3 submitted
Part 3 Approval
Disclaimer: All dates stated in the Commissioning Plan are subject to ERCOT approvals of Protocol Section 16.5 requirements and approvals of Part 1, Part 2, & Part 3 Checklists.
Note: Wind and Solar Resources are not required to submit PSS dates.

## Schedule S6
Commissioning Plan
|  |  |  | Resource Name: |  |  |  |  | Generic Resource Name
Commissioning Plan Section 6 (up to 3 Panels): Resource Detailed Commissioning Schedule
Event Day or Date | Cumulative Columns |  |  | Controls on Automatic |  |  | Max Leading MVAr on Automatic | Max Lagging MVAr on Automatic | Max Reactor Bank MVAr available | Max Capacitor Bank MVAr available | Static Reactive Devices (Manual/ Automatic) | Max DSTATCOM/DVAR/SVC MVAr on Automatic | MVAr Range on Automatic Only | Power Factor Range
| Number of Units | Resource MW | Resource MVA | [8 empty] | DVAR/SVC MVAr available on auto control
|  |  |  | PFR | AVR | VSS
2015-02-26 | 2 | 3 | 3.05 | N | N | N | 0 | 0 | -5 | 10 | Manual | 0 | 0 | -0.95 to +0.95
2015-02-28 | 4 | 6 | 6.1 | Y | Y | Y | -0.5 | 0.5 | -10 | 20 | Automatic | 0 | -0.5 to +0.6 | -0.95 to +0.96

## Capabilites S7
Commissioning Plan
|  | Resource Name: | Generic Resource Name
Commissioning Plan Section 7: Resource Design Capabilities
● | In accordance with Protocol Section 16.5(4), ERCOT reviews facility design capability. The current capabilities reviewed by ERCOT are listed in this section. ERCOT recommends that the Generic Resource Name Commissioning Plan provides confirmation of the following to help ERCOT evaluate the capabilities that will be available during the entire Commissioning Process.
Confirm Generic Resource Name will produce ±0.95 Power Factor Reactive at all MW levels between LSL and HSL. Protocol Section 8.1.1.2.1.4
Confirm Generic Resource Name has a Power System Stabilizer or equivalent included in its design. Protocol Section 3.15.3(4)
Confirm Generic Resource Name will provide Primary Frequency Response. Protocol Section 8.5.1.1 & 8.5.1.3
Confirm Generic Resource Name will operate with AVR in droop mode. Protocol Section 3.15
Confirm Generic Resource Name can respond to changes in the voltage profile using its AVR control mode. Protocol Section 3.15
Confirm the breaker interruption capability at Generic Resource Name is suitable to fault duty.
Confirm the transient volatage ride through at Generic Resource Name. Operating Guide Section 2.9
Confirm the under-frequency relays installed at Generic Resource Name meet the requirements in the ERCOT Operating Guides. Operating Guide Section 2.6.2
Comments:

## Notes S8
Commissioning Plan
|  | Resource Name: | Generic Resource Name
Commissioning Plan Section 8: Process Notes and Descriptions
● | Process notes and descriptions for the commissioning of Generic Resource Name.

## Instructions
Instructions ● Please complete all 8 Parts to this commissioning plan before emailing it to your ERCOT Client Services Representative. Include the GINR number at the end of the filename before the extension and include the GINR number in the subject line of the email. Once your ERCOT Client Services Representative has received your completed plan, then an internal ERCOT meeting will be scheduled to review (and possibly approve) your plan. ● Information provided in blue are examples or instructions that should be replaced and formatted in black. ● Section 1: To complete most fields in Part 1, please use information directly from the RARF. RE should include "(RE)" at the end of the name. QSE should include "(QSE)" at the end of the name. ● Section 2: There are 2 panels/pages to complete on this tab. ● Section 3: The maximum time allowed for completion of an orderly shut-down is 10 minutes. The maximum time allowed for completion of an emergency shut down is 5 minutes. ● Section 4: None as of this draft. ● Section 5: Replace the unit names with the actual Resource names from the RARF. ● Section 6: There are 3 panels/pages to complete (if necessary) on this tab. The "Event Day or Date" column could be used to number the event days (Example: 1 through 10). This could be used in case of delays during the plan to reference approximately how many days are left to complete the plan. ● Section 7: None as of this draft. ● Section 8: None as of this draft. ● Note: Many things on this form will be locked. If you need more room or choices on this form please consult with your ERCOT Client Services Representative.
Resource Fuel Categories
Biomass
Coal and Lignite
Combined Cycle
Diesel
Gas Steam
Hydro
Nuclear
Simple Cycle
Solar
Wind

## Version Information
Version | Description of Changes | Date | Author
1 | Original Draft | 2014-12-10 | Lloyd Prichard
1.1 | Formatting Edits on S1 and S5 | 2015-01-05 | Lloyd Prichard
1.2 | Formatting Edits (blue) on all tabs; New Examples on S2, S4 & S6; Disclaimer on S5; Updated Instructions tab, New Version tab, RARF notes on S1 and S5, Prompt changes on S2 and S4. | 2015-06-10 | Lloyd Prichard
1.3 | Addition of 20 MVA milestone on "S5" tab | 2015-06-17 | Patrick Coon
1.4 | Clarification of 20 MVA limit and changing example to "blue" | 2018-07-27 | Jay Teixeira and Ed Geer