## Slide 1
Supply Analysis Working Group Meeting
DC Tie Capacity Forecast Proposal
Pete Warnken
Manager, Resource Adequacy
December 12, 2018

## Slide 2: DC Tie Capacity Forecast Proposal
Calculate a capacity contribution percentage based on the following elements:
  Use SCED intervals during which the most recent summer EEA events have been declared (Currently August 2011)
  Base calculations on net imports (tie flow imports less tie flow exports)
  For the denominator, use DC tie capacity in place at the time of the summer EEA events
    1,106 MW during August 2011
  Calculate average net imports for each DC tie, then sum the averages
  Capacity Contribution = total net DC tie imports / DC tie capacity

## Slide 3: EEA Events Used for the Calculations
EEA Events, August 2011

## Slide 4: Capacity Contribution Calculation Inputs
Sample raw data extract from the Market Management System (MMS)

## Slide 5: Capacity Contribution Calculation Inputs
Sample extract of Excel Pivot Table for calculating average net imports for each DC tie

## Slide 6: Final Capacity Contribution Calculation
Final calculation inputs for the capacity contribution percentage:
Data and calcs are documented in the Excel workbook posted to the 12/12/2018 SAWG meeting webpage:
DC Tie Flows_August 2011 EEA Events_CapContribution.xlsx
CapContrib% = 831 / 1,106

## Slide 7: Handling of Planned DC Tie Projects
Makes sense to apply the capacity contribution percentage to expansions of existing DC ties
  Create a new CDR variable called PLANDCTIECAP
Large, unrelated projects like Southern Cross may need to be treated differently
  Include the capacity contribution for proposed DC tie capacity for which ERCOT has received (1) a signed IA, (2) written notice that notice-to-proceed provided by the developer, and (3) written notice that financial security provided to fund the interconnection facilities
  For example, use ERCOT SC planning study ‘max import’ assumption (714 MW) until better data is available?* How would this be crafted into Protocol language?
*See: http://www.ercot.com/content/wcm/key_documents_lists/140232/ERCOT-Southern_Cross_Flow_Assumptions.pptx