## Slide 1
Intra-Hour Wind Forecast Accuracy Updates
QMWG
Operations Analysis
10/15/2018

## Slide 2: Intra-Hour Wind Forecast Error (September 2018)
Performance Metric | Vendor A | Vendor B | Persistence*
Monthly MAE (MW) | 43 | 152 | 66
Monthly MAE when 5-Min. Wind Ramp > 100 MW | 91 | 305 | 178
* Persistence metric uses same historical data sent to vendors for fair comparison
AWS
Persistence

## Slide 3: Monthly Trends
* Persistence metric uses same historical data sent to vendors for fair comparison
Chart: MAE (MW)
| June 8-30 | July 1-31 | August 1-31 | September 1-30 | October 1-9
Persistence Baseline* | 92.8584 | 80.8692 | 84.1985 | 66.1441 | 88.3471
Vendor A Performance | 118.83 | 76.0414 | 62.4964 | 43.0555 | 60.1474
Vendor B Performance | 293.2726 | 172.0398 | 171.4898 | 151.7933 | 261.0266

## Slide 4: Monthly Trends (Wind Ramp > 100 MW)
* Persistence metric uses same historical data sent to vendors for fair comparison
Chart: MAE (MW)
| June 8-30 | July 1-31 | August 1-31 | September 1-30 | October 1-9
Persistence Baseline* | 187.6343 | 184.7022 | 186.0657 | 178.3351 | 182.527
Vendor A Performance | 145.4619 | 106.1049 | 106.8286 | 90.5821 | 101.7145
Vendor B Performance | 398.9676 | 298.2186 | 282.793 | 305.3081 | 386.7641

## Slide 5: SCR795 Update – Projected Wind Ramp Rate (PWRR)
Alarm: If wind is ramping in opposite direction than PWRR for X amount of intervals, i.e. not tracking, alarm is issued to operator
Persistence Option: Will go into persistence (i.e. PWRR = 0) if PWRR is not tracking with actual ramp for X+Y amount of intervals
Updated GTBD Equation:
  GTBD = Total Gen + K1*10*System Load Frequency Bias + K2*[(net non-conforming Load) – (net filtered non-conforming Load)] + K3*5*PLRR + K4*Regulation Deployed + K5*ACE Integral – K6*5*PWRR
|PWRR| ≤ Max PWRR Thresh

## Slide 6: Projected Wind Ramp Rate (PWRR) Trends
Ramp error will be actual error seen by SCED GTBD
Chart: MAE (MW)
| June 8-30 | July 1-31 | August 1-31 | September 1-30 | October 1-9
Actual Wind Ramp | 83.6555 | 72.1037 | 74.843 | 59.3406 | 80.2026
PWRR Error | 67.2876 | 53.1667 | 56.2466 | 44.3294 | 64.0713
* Only Vendor A’s forecast was used to calculate PWRR

## Slide 7: Projected Wind Ramp Rate (PWRR) Trends
Trends during times when Wind Ramp > 100 MW (both directions)
Chart: MAE (MW)
| June 8-30 | July 1-31 | August 1-31 | September 1-30 | October 1-9
Actual Wind Ramp | 161.8988 | 157.6822 | 157.0926 | 149.8086 | 157.7428
PWRR Error | 115.6389 | 99.1156 | 101.1892 | 94.1793 | 106.7724
* Only Vendor A’s forecast was used to calculate PWRR

## Slide 8: Example Impact of Projected Wind Ramp to GTBD
Chart: 5-Min. SCED GTBD Error Due to Wind Ramp (7/2/2018 22:00 - 7/3/2018 03:00)

## Slide 9: Next Steps
ERCOT will implement SCR795 during 2018 R5 between October 23 and October 25, 2018
Initially, K6 will be set to 0 so that it will not impact GTBD calculation
A market notice will be sent out prior to initial activation of K6 to a non-zero value
Market notice was sent out on September 24, 2018:
http://www.ercot.com/services/comm/mkt_notices/archives/2916